## summary + plot
| per cell (V) | pack (V) | dV as percentage |  | Energy (kWh)
datasheet minV | 2.5 | 20 | 68.49% | Ptot_15Ws | 3077057.16
datasheet maxV | 3.65 | 29.2 |  | Ptot_Ws | 46155857.4
|  |  |  | Ptot_Wm | 769264.29
BMS minV | 2.75 | 22 | 75.34% | Ptot_Wh | 12821.07
BMS maxV | 3.65 | 29.2 |  | Ptot_kWh | 12.82 | 108.9% | Actual vs rated pack capacity
[5 empty] | Ah | 250.3906 | Ah per cell
actual minV | 2.93 | 23.44 | 81.87% | Ah (12V) | 1001.6461
actual maxV | 3.58 | 28.63 |  | Ah (24V) | 500.823

## data_fullChg
Relative Time | CH101 | CH102
| pvVoltage | pvCurrent | pvPower
0 | 23.4398 | -0.026653 | -0.62474
15.0062 | 23.4403 | -0.026287 | -0.61619
30.0062 | 23.4405 | -0.025904 | -0.6072
45.0062 | 23.4407 | -0.026412 | -0.61911
60.0062 | 23.4409 | -0.026216 | -0.61452
75.0062 | 23.4411 | -0.026046 | -0.61054
90.0062 | 23.4412 | -0.025976 | -0.60892
105.0062 | 23.4414 | -0.025852 | -0.60601
120.0062 | 23.4416 | -0.025722 | -0.60296
135.0062 | 23.5206 | 7.2127 | 169.6461
150.0062 | 24.1839 | 29.9225 | 723.6403
165.0062 | 24.4117 | 33.1117 | 808.3111
180.0062 | 23.5545 | -0.026112 | -0.61506
195.0062 | 23.6553 | 6.2019 | 146.7065
210.0062 | 24.3711 | 28.2937 | 689.5487
225.0062 | 24.4921 | 36.1349 | 885.0199
240.0062 | 24.6503 | 36.0061 | 887.559
255.0062 | 24.6936 | 35.9452 | 887.6183
270.0062 | 24.7346 | 35.8819 | 887.5243
285.0062 | 24.776 | 35.8034 | 887.0624
300.0062 | 24.8109 | 35.8591 | 889.697
315.0062 | 24.8451 | 35.7807 | 888.9767
330.0062 | 24.8795 | 35.7078 | 888.3917
345.0062 | 24.9122 | 35.7153 | 889.7471
360.0062 | 24.9412 | 35.6998 | 890.3933
375.0062 | 24.97 | 35.5511 | 887.7126
390.0062 | 25 | 35.5712 | 889.2809
405.0062 | 25.0279 | 35.5044 | 888.6011
420.0062 | 25.0528 | 35.4841 | 888.9761
435.0062 | 25.0781 | 35.4682 | 889.4774
450.0062 | 25.1051 | 35.4267 | 889.3911
465.0062 | 25.129 | 35.404 | 889.6657
480.0062 | 25.153 | 35.4261 | 891.0735
495.0062 | 25.1763 | 35.3122 | 889.0288
510.0062 | 25.1985 | 35.2337 | 887.8344
525.0062 | 25.2208 | 35.3018 | 890.3403
540.0062 | 25.2428 | 35.2382 | 889.5134
555.0062 | 25.2628 | 35.21 | 889.5038
570.0062 | 25.285 | 35.1344 | 888.3736
585.0062 | 25.3024 | 35.1352 | 889.0056
600.0062 | 25.3257 | 35.2084 | 891.6776
615.0062 | 25.3445 | 35.0725 | 888.8966
630.0062 | 25.3652 | 35.0824 | 889.871
645.0062 | 25.3816 | 35.0878 | 890.585
660.0062 | 25.3993 | 35.0023 | 889.0324
675.0062 | 25.4188 | 35.0267 | 890.3365
690.0062 | 25.4377 | 34.9924 | 890.1281
705.0062 | 25.4545 | 34.9592 | 889.8675
720.0062 | 25.473 | 34.9214 | 889.5523
735.0062 | 25.4892 | 34.9004 | 889.5856
750.0062 | 25.5076 | 34.8818 | 889.7508
765.0062 | 25.5257 | 34.8593 | 889.8074
780.0062 | 25.5419 | 28.191 | 720.052
795.0062 | 25.4381 | 28.5612 | 726.5424
810.0062 | 25.5679 | 34.8071 | 889.9436
825.0062 | 25.5839 | 34.8613 | 891.8881
840.0062 | 25.6011 | 34.78 | 890.4058
855.0062 | 25.6173 | 34.671 | 888.1774
870.0062 | 25.6333 | 34.618 | 887.3755
885.0062 | 25.6513 | 34.7463 | 891.2865
900.0062 | 25.663 | 34.7648 | 892.1706
915.0062 | 25.678 | 34.6509 | 889.765
930.0062 | 25.6932 | 34.6773 | 890.9719
945.0062 | 25.7078 | 34.6877 | 891.7453
960.0062 | 25.7208 | 34.6141 | 890.3044
975.0062 | 25.7374 | 34.5856 | 890.1433
990.0062 | 25.7506 | 34.6125 | 891.2928
1005.0062 | 25.7666 | 34.59 | 891.2654
1020.0062 | 25.7777 | 34.5177 | 889.7875
1035.0062 | 25.7947 | 34.5479 | 891.1548
1050.0062 | 25.8082 | 34.4297 | 888.567
1065.0062 | 25.823 | 34.4459 | 889.4969
1080.0062 | 25.8385 | 34.3962 | 888.7443
1095.0062 | 25.8512 | 34.4223 | 889.8577
1110.0062 | 25.8647 | 34.4579 | 891.2439
1125.0062 | 25.8784 | 34.4393 | 891.2334
1140.0062 | 25.8926 | 34.3665 | 889.8386
1155.0062 | 25.9059 | 34.4346 | 892.0584
1170.0062 | 25.9182 | 34.4216 | 892.1446
1185.0062 | 25.9288 | 34.2957 | 889.2452
1200.0062 | 25.9441 | 34.3713 | 891.7322
1215.0062 | 25.953 | 34.3631 | 891.8256
1230.0062 | 25.9687 | 34.2328 | 888.9796
1245.0062 | 25.9812 | 34.2474 | 889.7898
1260.0062 | 25.9934 | 34.2155 | 889.3767
1275.0062 | 26.0043 | 34.2096 | 889.597
1290.0062 | 26.0181 | 34.2766 | 891.8134
1305.0062 | 26.0304 | 34.2189 | 890.7298
1320.0062 | 26.0423 | 34.2566 | 892.1204
1335.0062 | 26.0531 | 34.205 | 891.1449
1350.0062 | 26.0643 | 34.1668 | 890.5352
1365.0062 | 26.0785 | 34.1608 | 890.8651
1380.0062 | 26.0663 | 28.0366 | 730.8112
1395.0062 | 25.925 | 28.5201 | 739.3822
1410.0062 | 26.1044 | 34.1142 | 890.5295
1425.0062 | 26.118 | 34.1364 | 891.5748
1440.0062 | 26.1312 | 34.1302 | 891.8612
1455.0062 | 26.1417 | 34.0336 | 889.6961
1470.0062 | 26.1544 | 34.0963 | 891.7683
1485.0062 | 26.1644 | 34.0511 | 890.9254
1500.0062 | 26.1747 | 33.9644 | 889.0077
1515.0062 | 26.1836 | 34.0193 | 890.7482
1530.0062 | 26.1978 | 34.0203 | 891.2581
1545.0062 | 26.2088 | 34.0017 | 891.1444
1560.0062 | 26.2188 | 33.974 | 890.757
1575.0062 | 26.2286 | 33.9512 | 890.4949
1590.0062 | 26.2389 | 33.9996 | 892.1141
1605.0062 | 26.2492 | 33.9606 | 891.4373
1620.0062 | 26.2619 | 33.953 | 891.671
1635.0062 | 26.2702 | 33.9452 | 891.749
1650.0062 | 26.2818 | 33.9252 | 891.6159
1665.0062 | 26.2903 | 33.8241 | 889.246
1680.0062 | 26.2986 | 33.8747 | 890.8576
1695.0062 | 26.3073 | 33.8939 | 891.6582
1710.0062 | 26.3162 | 33.8396 | 890.5314
1725.0062 | 26.3263 | 33.8673 | 891.6028
1740.0062 | 26.3384 | 33.8992 | 892.8513
1755.0062 | 26.3479 | 33.8271 | 891.2743
1770.0062 | 26.3551 | 33.7864 | 890.4434
1785.0062 | 26.3647 | 33.7889 | 890.8332
1800.0062 | 26.3767 | 33.7438 | 890.0491
1815.0062 | 26.3866 | 33.8007 | 891.8847
1830.0062 | 26.3941 | 33.8036 | 892.2148
1845.0062 | 26.4056 | 33.8321 | 893.3569
1860.0062 | 26.415 | 33.73 | 890.9792
1875.0062 | 26.424 | 33.7251 | 891.152
1890.0062 | 26.4324 | 33.6764 | 890.1501
1905.0062 | 26.4422 | 33.6763 | 890.4764
1920.0062 | 26.4511 | 33.7178 | 891.8742
1935.0062 | 26.4582 | 33.6983 | 891.5968
1950.0062 | 26.468 | 33.6675 | 891.1108
1965.0062 | 26.4752 | 33.6726 | 891.4904
1980.0062 | 26.4148 | 28.8398 | 761.7986
1995.0062 | 26.4902 | 33.5732 | 889.3598
2010.0062 | 26.4978 | 33.6018 | 890.3728
2025.0062 | 26.5061 | 33.5713 | 889.8469
2040.0062 | 26.5121 | 33.5137 | 888.518
2055.0062 | 26.5221 | 33.6345 | 892.0569
2070.0062 | 26.5322 | 33.6081 | 891.6966
2085.0062 | 26.5416 | 33.597 | 891.7185
2100.0062 | 26.5473 | 33.5633 | 891.0136
2115.0062 | 26.5569 | 33.5892 | 892.0258
2130.0062 | 26.565 | 33.5781 | 892.0039
2145.0062 | 26.5724 | 33.5081 | 890.3899
2160.0062 | 26.5821 | 33.5381 | 891.5146
2175.0062 | 26.5888 | 33.6058 | 893.5381
2190.0062 | 26.5983 | 33.5656 | 892.7857
2205.0062 | 26.6056 | 33.5601 | 892.8865
2220.0062 | 26.6145 | 33.548 | 892.8633
2235.0062 | 26.6213 | 33.4389 | 890.1862
2250.0062 | 26.6255 | 33.426 | 889.984
2265.0062 | 26.6336 | 33.5664 | 893.9938
2280.0062 | 26.6407 | 33.4464 | 891.036
2295.0062 | 26.65 | 33.4491 | 891.4174
2310.0062 | 26.6579 | 33.4762 | 892.4041
2325.0062 | 26.6651 | 33.517 | 893.7338
2340.0062 | 26.6725 | 33.4421 | 891.9825
2355.0062 | 26.6791 | 33.4654 | 892.8262
2370.0062 | 26.6867 | 33.4085 | 891.5602
2385.0062 | 26.6926 | 33.3441 | 890.042
2400.0062 | 26.6969 | 33.324 | 889.6472
2415.0062 | 26.703 | 33.3545 | 890.6641
2430.0062 | 26.7096 | 33.3497 | 890.757
2445.0062 | 26.7167 | 33.4092 | 892.5837
2460.0062 | 26.723 | 33.419 | 893.055
2475.0062 | 26.73 | 33.3678 | 891.9238
2490.0062 | 26.736 | 33.3167 | 890.7553
2505.0062 | 26.7408 | 33.3463 | 891.7073
2520.0062 | 26.7493 | 33.3273 | 891.4819
2535.0062 | 26.7535 | 33.354 | 892.3345
2550.0062 | 26.7587 | 33.3518 | 892.4517
2565.0062 | 26.7643 | 33.332 | 892.106
2580.0062 | 26.7525 | 28.0688 | 750.91
2595.0062 | 26.601 | 30.0608 | 799.6486
2610.0062 | 26.7802 | 33.2426 | 890.2438
2625.0062 | 26.7892 | 33.276 | 891.4353
2640.0062 | 26.7957 | 33.2999 | 892.2951
2655.0062 | 26.801 | 33.2318 | 890.6445
2670.0062 | 26.8058 | 33.3003 | 892.6417
2685.0062 | 26.8067 | 33.2776 | 892.0604
2700.0062 | 26.8134 | 33.263 | 891.8939
2715.0062 | 26.8161 | 33.2354 | 891.2442
2730.0062 | 26.8216 | 33.3231 | 893.7771
2745.0062 | 26.8214 | 33.3017 | 893.1964
2760.0062 | 26.824 | 33.2095 | 890.8106
2775.0062 | 26.8249 | 33.227 | 891.3095
2790.0062 | 26.8296 | 33.2858 | 893.0438
2805.0062 | 26.8309 | 33.2072 | 890.9787
2820.0062 | 26.8325 | 33.193 | 890.6521
2835.0062 | 26.8323 | 33.2637 | 892.5441
2850.0062 | 26.834 | 33.2878 | 893.2447
2865.0062 | 26.8386 | 33.1221 | 888.9499
2880.0062 | 26.84 | 33.2111 | 891.385
2895.0062 | 26.8418 | 33.2281 | 891.904
2910.0062 | 26.843 | 33.2334 | 892.0827
2925.0062 | 26.8463 | 33.2503 | 892.6476
2940.0062 | 26.8466 | 33.2267 | 892.0233
2955.0062 | 26.8463 | 33.2471 | 892.5614
2970.0062 | 26.8476 | 33.1424 | 889.7947
2985.0062 | 26.8505 | 33.1668 | 890.5456
3000.0062 | 26.8518 | 33.1989 | 891.4497
3015.0062 | 26.8505 | 33.1516 | 890.1357
3030.0062 | 26.8539 | 33.2216 | 892.1272
3045.0062 | 26.8542 | 33.2563 | 893.0721
3060.0062 | 26.8559 | 33.2375 | 892.6216
3075.0062 | 26.8551 | 33.1957 | 891.474
3090.0062 | 26.8554 | 33.2372 | 892.5994
3105.0062 | 26.8588 | 33.1601 | 890.6386
3120.0062 | 26.8602 | 33.1638 | 890.7887
3135.0062 | 26.8601 | 33.2777 | 893.8443
3150.0062 | 26.8597 | 33.204 | 891.8484
3165.0062 | 26.859 | 33.206 | 891.8797
3180.0062 | 26.8355 | 27.3047 | 732.736
3195.0062 | 26.6805 | 30.2148 | 806.1454
3210.0062 | 26.8556 | 33.2231 | 892.2274
3225.0062 | 26.8591 | 33.176 | 891.0764
3240.0062 | 26.8621 | 33.2046 | 891.9473
3255.0062 | 26.8632 | 33.2041 | 891.9689
3270.0062 | 26.8657 | 33.2509 | 893.3081
3285.0062 | 26.8641 | 33.1964 | 891.7922
3300.0062 | 26.8658 | 33.2089 | 892.1833
3315.0062 | 26.866 | 33.2637 | 893.6634
3330.0062 | 26.865 | 33.2776 | 894.0042
3345.0062 | 26.8682 | 33.1757 | 891.3718
3360.0062 | 26.8677 | 33.137 | 890.3132
3375.0062 | 26.8693 | 33.1592 | 890.9649
3390.0062 | 26.8705 | 33.2036 | 892.1966
3405.0062 | 26.8706 | 33.2462 | 893.3455
3420.0062 | 26.8689 | 33.2748 | 894.0574
3435.0062 | 26.8715 | 33.261 | 893.7737
3450.0062 | 26.8733 | 33.2767 | 894.2567
3465.0062 | 26.8729 | 33.2186 | 892.6806
3480.0062 | 26.8721 | 33.2041 | 892.2638
3495.0062 | 26.8722 | 33.2148 | 892.5536
3510.0062 | 26.8739 | 33.2018 | 892.2635
3525.0062 | 26.8725 | 33.2383 | 893.1955
3540.0062 | 26.8746 | 33.2063 | 892.4065
3555.0062 | 26.8746 | 33.234 | 893.1521
3570.0062 | 26.8751 | 33.2113 | 892.5585
3585.0062 | 26.8737 | 33.1226 | 890.1261
3600.0062 | 26.8756 | 33.1476 | 890.8624
3615.0062 | 26.8752 | 33.1316 | 890.4206
3630.0062 | 26.8733 | 33.132 | 890.3678
3645.0062 | 26.8757 | 33.1813 | 891.7707
3660.0062 | 26.8764 | 33.1074 | 889.8067
3675.0062 | 26.876 | 33.2248 | 892.9496
3690.0062 | 26.8774 | 33.2506 | 893.6905
3705.0062 | 26.8776 | 33.2353 | 893.2846
3720.0062 | 26.875 | 33.112 | 889.8841
3735.0062 | 26.8789 | 33.1967 | 892.2927
3750.0062 | 26.8785 | 33.1859 | 891.9846
3765.0062 | 26.8814 | 33.208 | 892.6786
3780.0062 | 26.7021 | 28.3785 | 757.7644
3795.0062 | 26.6987 | 33.1911 | 886.1582
3810.0062 | 26.8807 | 33.2164 | 892.881
3825.0062 | 26.8784 | 33.2387 | 893.402
3840.0062 | 26.8827 | 33.2704 | 894.3987
3855.0062 | 26.8816 | 33.1165 | 890.2246
3870.0062 | 26.8822 | 33.1105 | 890.0846
3885.0062 | 26.8845 | 33.14 | 890.9537
3900.0062 | 26.8835 | 33.1506 | 891.2026
3915.0062 | 26.8854 | 33.1303 | 890.7223
3930.0062 | 26.8873 | 33.2339 | 893.5714
3945.0062 | 26.8883 | 33.1815 | 892.1931
3960.0062 | 26.8865 | 33.2145 | 893.021
3975.0062 | 26.8897 | 33.2305 | 893.5603
3990.0062 | 26.8895 | 33.1788 | 892.1598
4005.0062 | 26.8881 | 33.1835 | 892.2418
4020.0062 | 26.8887 | 33.2259 | 893.4007
4035.0062 | 26.8879 | 33.1909 | 892.4328
4050.0062 | 26.8903 | 33.1833 | 892.3103
4065.0062 | 26.8908 | 33.1946 | 892.6297
4080.0062 | 26.8894 | 33.2139 | 893.1034
4095.0062 | 26.8896 | 33.1814 | 892.2364
4110.0062 | 26.8906 | 33.1522 | 891.4811
4125.0062 | 26.8905 | 33.1581 | 891.6372
4140.0062 | 26.892 | 33.1847 | 892.4045
4155.0062 | 26.8909 | 33.1071 | 890.2788
4170.0062 | 26.8932 | 33.1777 | 892.2534
4185.0062 | 26.8927 | 33.2395 | 893.8998
4200.0062 | 26.8944 | 33.1319 | 891.0634
4215.0062 | 26.8937 | 33.1754 | 892.2074
4230.0063 | 26.8956 | 33.1181 | 890.7292
4245.0062 | 26.8964 | 33.2073 | 893.1577
4260.0062 | 26.8939 | 33.1631 | 891.8853
4275.0062 | 26.8971 | 33.1643 | 892.0236
4290.0062 | 26.8956 | 33.1876 | 892.6029
4305.0062 | 26.8978 | 33.1866 | 892.6476
4320.0062 | 26.898 | 33.2213 | 893.5837
4335.0062 | 26.8967 | 33.2392 | 894.0274
4350.0062 | 26.8954 | 33.1387 | 891.2794
4365.0062 | 26.897 | 33.2014 | 893.0166
4380.0062 | 26.8315 | 26.9597 | 723.3693
4395.0062 | 26.7449 | 27.8696 | 745.3706
4410.0062 | 26.8934 | 33.1969 | 892.7781
4425.0062 | 26.8975 | 33.1067 | 890.4875
4440.0062 | 26.899 | 33.1117 | 890.6706
4455.0062 | 26.8994 | 33.1757 | 892.4063
4470.0062 | 26.9012 | 33.189 | 892.8244
4485.0062 | 26.9022 | 33.1627 | 892.1488
4500.0062 | 26.9066 | 33.105 | 890.7425
4515.0062 | 26.9069 | 33.1407 | 891.7143
4530.0062 | 26.9063 | 33.1774 | 892.6818
4545.0062 | 26.906 | 33.1249 | 891.2577
4560.0062 | 26.9064 | 33.1997 | 893.2843
4575.0062 | 26.907 | 33.1991 | 893.288
4590.0062 | 26.9067 | 33.1197 | 891.1422
4605.0062 | 26.9078 | 33.1177 | 891.1244
4620.0062 | 26.909 | 33.1408 | 891.7871
4635.0062 | 26.9105 | 33.2017 | 893.4762
4650.0062 | 26.913 | 33.1413 | 891.9343
4665.0062 | 26.9126 | 33.1561 | 892.3169
4680.0062 | 26.9127 | 33.1499 | 892.1513
4695.0062 | 26.912 | 33.1786 | 892.9009
4710.0062 | 26.9124 | 33.0348 | 889.0451
4725.0062 | 26.912 | 33.1793 | 892.9205
4740.0062 | 26.9141 | 33.1885 | 893.2365
4755.0062 | 26.9153 | 33.1828 | 893.1243
4770.0062 | 26.9138 | 33.141 | 891.9516
4785.0062 | 26.9136 | 33.1463 | 892.0846
4800.0062 | 26.9118 | 33.163 | 892.4753
4815.0062 | 26.9153 | 33.0965 | 890.8023
4830.0062 | 26.9177 | 33.1495 | 892.3092
4845.0062 | 26.9179 | 33.1093 | 891.232
4860.0062 | 26.9162 | 33.1523 | 892.3333
4875.0062 | 26.9189 | 33.1921 | 893.4952
4890.0062 | 26.9186 | 33.1957 | 893.5818
4905.0062 | 26.9189 | 33.1546 | 892.484
4920.0062 | 26.9206 | 33.1688 | 892.9221
4935.0062 | 26.9205 | 33.1125 | 891.4024
4950.0062 | 26.9205 | 33.1481 | 892.3609
4965.0062 | 26.9195 | 33.1188 | 891.5414
4980.0062 | 26.7846 | 26.8835 | 720.0659
4995.0062 | 26.7924 | 33.1243 | 887.4785
5010.0062 | 26.918 | 33.1396 | 892.0507
5025.0062 | 26.9203 | 33.185 | 893.3496
5040.0062 | 26.9233 | 33.1279 | 891.9132
5055.0062 | 26.9223 | 33.1612 | 892.7756
5070.0062 | 26.9239 | 33.1013 | 891.2159
5085.0062 | 26.9253 | 33.1306 | 892.0491
5100.0062 | 26.9258 | 33.0998 | 891.2366
5115.0062 | 26.9272 | 33.1331 | 892.1809
5130.0062 | 26.9279 | 33.1964 | 893.9085
5145.0062 | 26.9309 | 33.0843 | 890.9913
5160.0062 | 26.9316 | 33.1646 | 893.1757
5175.0062 | 26.9299 | 33.005 | 888.8211
5190.0062 | 26.9324 | 33.1413 | 892.5755
5205.0062 | 26.9318 | 33.096 | 891.3347
5220.0062 | 26.9331 | 33.0799 | 890.9465
5235.0062 | 26.9328 | 33.1543 | 892.9392
5250.0062 | 26.9345 | 33.0974 | 891.462
5265.0062 | 26.9351 | 33.1213 | 892.1258
5280.0062 | 26.934 | 33.1436 | 892.6891
5295.0062 | 26.9384 | 33.151 | 893.0362
5310.0062 | 26.94 | 33.121 | 892.2817
5325.0062 | 26.9405 | 33.1574 | 893.2774
5340.0062 | 26.9391 | 33.1098 | 891.947
5355.0062 | 26.9403 | 33.0739 | 891.0201
5370.0062 | 26.9417 | 33.0932 | 891.5866
5385.0062 | 26.9421 | 33.1336 | 892.6889
5400.0062 | 26.9423 | 33.0898 | 891.5172
5415.0062 | 26.9439 | 33.1336 | 892.7494
5430.0062 | 26.9457 | 33.1365 | 892.8848
5445.0063 | 26.9454 | 33.0976 | 891.8279
5460.0062 | 26.9447 | 33.0944 | 891.7161
5475.0062 | 26.947 | 33.1158 | 892.3718
5490.0062 | 26.9488 | 33.0875 | 891.6691
5505.0062 | 26.9498 | 33.1071 | 892.2287
5520.0062 | 26.9499 | 33.0488 | 890.6596
5535.0062 | 26.9496 | 33.142 | 893.1643
5550.0062 | 26.9511 | 33.0937 | 891.9103
5565.0062 | 26.9495 | 33.0878 | 891.7001
5580.0062 | 26.8328 | 27.4088 | 735.4567
5595.0062 | 26.8519 | 26.9923 | 724.7942
5610.0062 | 26.9494 | 33.0905 | 891.7674
5625.0062 | 26.9534 | 33.1199 | 892.6954
5640.0062 | 26.9566 | 33.1424 | 893.4068
5655.0062 | 26.9559 | 33.0597 | 891.1548
5670.0062 | 26.9577 | 33.1334 | 893.2013
5685.0062 | 26.9625 | 33.037 | 890.7618
5700.0062 | 26.9601 | 33.1446 | 893.5821
5715.0062 | 26.9599 | 33.1711 | 894.2919
5730.0062 | 26.9612 | 33.1765 | 894.4798
5745.0062 | 26.9636 | 33.0956 | 892.3769
5760.0062 | 26.9647 | 33.1744 | 894.5372
5775.0062 | 26.964 | 33.1207 | 893.0659
5790.0062 | 26.9651 | 33.0957 | 892.4273
5805.0062 | 26.967 | 33.0919 | 892.3886
5820.0062 | 26.9667 | 33.1258 | 893.2958
5835.0062 | 26.9684 | 33.1381 | 893.683
5850.0062 | 26.968 | 33.01 | 890.2128
5865.0062 | 26.968 | 33.0771 | 892.0252
5880.0062 | 26.972 | 33.0545 | 891.5459
5895.0062 | 26.9748 | 33.0654 | 891.9331
5910.0062 | 26.9786 | 33.1177 | 893.4709
5925.0062 | 26.9794 | 33.069 | 892.1827
5940.0062 | 26.9818 | 33.0876 | 892.7622
5955.0062 | 26.9822 | 33.1034 | 893.2043
5970.0062 | 26.9815 | 33.0798 | 892.5424
5985.0062 | 26.9826 | 33.0789 | 892.554
6000.0062 | 26.9821 | 33.0805 | 892.5833
6015.0062 | 26.9853 | 33.095 | 893.078
6030.0062 | 26.9872 | 33.0778 | 892.6781
6045.0062 | 26.9859 | 33.0584 | 892.1114
6060.0062 | 26.9869 | 33.1121 | 893.5903
6075.0062 | 26.9908 | 33.0583 | 892.2678
6090.0062 | 26.9906 | 33.0775 | 892.7831
6105.0062 | 26.992 | 33.0161 | 891.1719
6120.0062 | 26.9927 | 33.0533 | 892.1971
6135.0062 | 26.9905 | 33.0463 | 891.9387
6150.0062 | 26.9926 | 33.0998 | 893.4523
6165.0062 | 26.9928 | 33.0701 | 892.6544
6180.0062 | 26.9181 | 27.9383 | 752.0454
6195.0062 | 26.9309 | 33.1083 | 891.6355
6210.0062 | 26.9936 | 33.0396 | 891.857
6225.0062 | 26.9971 | 33.0374 | 891.9131
6240.0062 | 26.998 | 33.0786 | 893.0565
6255.0062 | 26.9996 | 33.0195 | 891.5116
6270.0062 | 27.0034 | 33.018 | 891.5982
6285.0062 | 27.0019 | 33.0112 | 891.3673
6300.0062 | 27.0034 | 33.0692 | 892.9781
6315.0062 | 27.0044 | 33.0308 | 891.9779
6330.0062 | 27.0067 | 33.0367 | 892.2127
6345.0062 | 27.0091 | 33.033 | 892.1901
6360.0062 | 27.0106 | 32.984 | 890.9197
6375.0062 | 27.0096 | 33.0443 | 892.5135
6390.0062 | 27.0109 | 33.1293 | 894.8518
6405.0062 | 27.0129 | 33.0329 | 892.3155
6420.0062 | 27.015 | 33.1014 | 894.2365
6435.0062 | 27.0168 | 33.021 | 892.1199
6450.0062 | 27.0178 | 32.9682 | 890.7289
6465.0062 | 27.0182 | 32.9937 | 891.4301
6480.0062 | 27.0174 | 33.0351 | 892.5227
6495.0062 | 27.0208 | 33.0513 | 893.0723
6510.0062 | 27.0255 | 33.0537 | 893.2916
6525.0062 | 27.025 | 33.0094 | 892.079
6540.0062 | 27.0246 | 33.0231 | 892.4375
6555.0062 | 27.0256 | 33.0149 | 892.2469
6570.0062 | 27.0272 | 33.023 | 892.5178
6585.0062 | 27.027 | 32.967 | 890.9994
6600.0062 | 27.0274 | 32.9927 | 891.7086
6615.0062 | 27.0296 | 32.9877 | 891.6423
6630.0062 | 27.0292 | 33.0201 | 892.5062
6645.0062 | 27.0337 | 32.9768 | 891.4855
6660.0062 | 27.0344 | 32.9397 | 890.504
6675.0062 | 27.0347 | 32.9971 | 892.0648
6690.0062 | 27.0369 | 32.9882 | 891.9001
6705.0062 | 27.0368 | 33.0644 | 893.9555
6720.0062 | 27.0433 | 33.0339 | 893.3483
6735.0062 | 27.0437 | 32.9698 | 891.6264
6750.0062 | 27.0461 | 33.0191 | 893.0373
6765.0062 | 27.0443 | 33.0207 | 893.0228
6780.0062 | 26.8808 | 27.4339 | 737.4458
6795.0062 | 26.9297 | 26.4102 | 711.2178
6810.0062 | 27.0441 | 33.0088 | 892.6934
6825.0062 | 27.0475 | 33.045 | 893.7844
6840.0062 | 27.0506 | 32.9648 | 891.7166
6855.0062 | 27.0524 | 32.9435 | 891.2003
6870.0062 | 27.0514 | 33.0152 | 893.1072
6885.0062 | 27.0535 | 33.0064 | 892.9384
6900.0062 | 27.0579 | 32.929 | 890.9888
6915.0062 | 27.0602 | 32.9714 | 892.2124
6930.0062 | 27.0599 | 32.9772 | 892.3605
6945.0062 | 27.0603 | 32.9596 | 891.8966
6960.0062 | 27.0611 | 33.0121 | 893.3458
6975.0062 | 27.062 | 32.9943 | 892.8932
6990.0062 | 27.0644 | 32.9664 | 892.2139
7005.0062 | 27.0662 | 32.9862 | 892.8125
7020.0062 | 27.0662 | 33.0075 | 893.3871
7035.0062 | 27.0688 | 32.893 | 890.3743
7050.0062 | 27.073 | 33.005 | 893.5464
7065.0062 | 27.0711 | 32.9344 | 891.5691
7080.0062 | 27.0731 | 32.9907 | 893.1624
7095.0062 | 27.0747 | 32.9631 | 892.4673
7110.0062 | 27.0765 | 32.9987 | 893.4902
7125.0062 | 27.077 | 32.8891 | 890.5386
7140.0062 | 27.0787 | 32.9082 | 891.1126
7155.0062 | 27.0782 | 33.0069 | 893.7685
7170.0062 | 27.0822 | 32.9868 | 893.3535
7185.0062 | 27.0849 | 32.9485 | 892.4087
7200.0062 | 27.0854 | 32.8801 | 890.5685
7215.0062 | 27.0843 | 32.9798 | 893.2352
7230.0062 | 27.0861 | 32.9615 | 892.7981
7245.0062 | 27.0874 | 32.9042 | 891.2895
7260.0062 | 27.0864 | 32.9085 | 891.3749
7275.0062 | 27.09 | 32.9887 | 893.6651
7290.0062 | 27.0915 | 32.8893 | 891.0196
7305.0062 | 27.0909 | 32.9684 | 893.1446
7320.0062 | 27.0932 | 32.9672 | 893.1879
7335.0062 | 27.0955 | 32.9075 | 891.645
7350.0062 | 27.0954 | 32.916 | 891.8732
7365.0062 | 27.0964 | 32.9846 | 893.763
7380.0062 | 26.9727 | 26.6028 | 717.549
7395.0062 | 27.0994 | 32.9648 | 893.3256
7410.0062 | 27.1025 | 32.9576 | 893.2332
7425.0062 | 27.1031 | 32.9637 | 893.4175
7440.0062 | 27.1052 | 32.8721 | 891.0068
7455.0062 | 27.1063 | 32.9338 | 892.7124
7470.0062 | 27.109 | 32.9476 | 893.1757
7485.0062 | 27.1122 | 32.9223 | 892.596
7500.0062 | 27.1121 | 32.9493 | 893.3224
7515.0062 | 27.1125 | 32.878 | 891.4056
7530.0062 | 27.1128 | 32.9471 | 893.2877
7545.0062 | 27.1123 | 32.9523 | 893.4138
7560.0062 | 27.1178 | 32.9278 | 892.9275
7575.0062 | 27.1196 | 32.9552 | 893.7319
7590.0062 | 27.1195 | 32.9111 | 892.5323
7605.0062 | 27.1209 | 32.8812 | 891.7674
7620.0062 | 27.1208 | 32.7759 | 888.9077
7635.0062 | 27.1229 | 32.917 | 892.8031
7650.0062 | 27.1221 | 32.7375 | 887.9095
7665.0062 | 27.1263 | 32.9595 | 894.0709
7680.0062 | 27.127 | 32.9405 | 893.5782
7695.0062 | 27.1287 | 32.8237 | 890.4649
7710.0062 | 27.1296 | 32.8803 | 892.0272
7725.0062 | 27.132 | 32.9083 | 892.8672
7740.0062 | 27.1329 | 32.9698 | 894.5646
7755.0062 | 27.1344 | 32.9499 | 894.0741
7770.0062 | 27.136 | 32.8726 | 892.0307
7785.0062 | 27.1363 | 32.9193 | 893.3069
7800.0062 | 27.1376 | 32.8512 | 891.5043
7815.0062 | 27.138 | 32.8803 | 892.3058
7830.0062 | 27.142 | 32.9728 | 894.9473
7845.0062 | 27.1436 | 32.8769 | 892.3973
7860.0062 | 27.1451 | 32.92 | 893.6151
7875.0062 | 27.1468 | 32.8915 | 892.9015
7890.0062 | 27.1472 | 32.8517 | 891.8297
7905.0062 | 27.1485 | 32.8683 | 892.326
7920.0062 | 27.1512 | 32.8203 | 891.1112
7935.0062 | 27.1541 | 32.8377 | 891.6775
7950.0062 | 27.1507 | 32.8462 | 891.7977
7965.0062 | 27.155 | 32.9069 | 893.5886
7980.0062 | 26.9991 | 27.4646 | 741.5207
7995.0062 | 27.1531 | 32.8918 | 893.1138
8010.0062 | 27.1585 | 32.8675 | 892.6331
8025.0062 | 27.1621 | 32.8383 | 891.957
8040.0062 | 27.1641 | 32.8509 | 892.364
8055.0062 | 27.1651 | 32.6912 | 888.06
8070.0062 | 27.1678 | 32.8865 | 893.4522
8085.0062 | 27.1678 | 32.8369 | 892.1059
8100.0062 | 27.17 | 32.8186 | 891.68
8115.0062 | 27.1696 | 32.8535 | 892.617
8130.0062 | 27.1728 | 32.7371 | 889.5585
8145.0062 | 27.172 | 32.8851 | 893.5536
8160.0062 | 27.1745 | 32.7936 | 891.1497
8175.0062 | 27.179 | 32.7596 | 890.3726
8190.0062 | 27.179 | 32.7792 | 890.9054
8205.0062 | 27.1806 | 32.8971 | 894.1632
8220.0062 | 27.1817 | 32.9041 | 894.3902
8235.0062 | 27.181 | 32.8052 | 891.6789
8250.0062 | 27.184 | 32.9087 | 894.5884
8265.0062 | 27.1864 | 32.8741 | 893.7295
8280.0062 | 27.1879 | 32.8466 | 893.0319
8295.0062 | 27.1897 | 32.791 | 891.5763
8310.0062 | 27.1891 | 32.8607 | 893.455
8325.0062 | 27.1902 | 32.8329 | 892.731
8340.0062 | 27.1891 | 32.8148 | 892.2043
8355.0062 | 27.192 | 32.7982 | 891.8467
8370.0062 | 27.1948 | 32.8558 | 893.5067
8385.0062 | 27.1978 | 32.8753 | 894.1345
8400.0062 | 27.1978 | 32.7786 | 891.5057
8415.0062 | 27.202 | 32.7915 | 891.9952
8430.0062 | 27.2025 | 32.845 | 893.4654
8445.0062 | 27.2042 | 32.8697 | 894.1938
8460.0062 | 27.2047 | 32.7811 | 891.7992
8475.0062 | 27.206 | 32.7924 | 892.1502
8490.0062 | 27.2065 | 32.8042 | 892.4864
8505.0062 | 27.2071 | 32.8363 | 893.3814
8520.0062 | 27.2094 | 32.796 | 892.3597
8535.0062 | 27.2093 | 32.7818 | 891.9703
8550.0062 | 27.2111 | 32.8607 | 894.1748
8565.0062 | 27.2123 | 32.8254 | 893.2559
8580.0062 | 27.0722 | 27.8797 | 754.7661
8595.0062 | 27.0494 | 28.7194 | 776.8416
8610.0062 | 27.2103 | 32.8431 | 893.6722
8625.0062 | 27.2129 | 32.8007 | 892.6032
8640.0062 | 27.2142 | 32.7164 | 890.3522
8655.0062 | 27.2164 | 32.7901 | 892.4289
8670.0062 | 27.2172 | 32.778 | 892.1257
8685.0062 | 27.2197 | 32.7436 | 891.2689
8700.0062 | 27.221 | 32.8276 | 893.5999
8715.0062 | 27.2227 | 32.8232 | 893.5346
8730.0062 | 27.2238 | 32.7434 | 891.398
8745.0062 | 27.226 | 32.7787 | 892.4327
8760.0062 | 27.2302 | 32.8039 | 893.2579
8775.0062 | 27.2285 | 32.7129 | 890.722
8790.0062 | 27.2309 | 32.7383 | 891.4947
8805.0062 | 27.2311 | 32.7409 | 891.5727
8820.0062 | 27.2324 | 32.7451 | 891.7271
8835.0062 | 27.2313 | 32.7969 | 893.1021
8850.0062 | 27.2364 | 32.7698 | 892.5309
8865.0062 | 27.2345 | 32.7842 | 892.8627
8880.0062 | 27.2339 | 32.7677 | 892.3941
8895.0062 | 27.2396 | 32.7935 | 893.2823
8910.0062 | 27.2366 | 32.7098 | 890.9023
8925.0062 | 27.2388 | 32.7283 | 891.4783
8940.0062 | 27.2407 | 32.7642 | 892.5202
8955.0062 | 27.2407 | 32.7616 | 892.4504
8970.0062 | 27.2424 | 32.6677 | 889.945
8985.0062 | 27.2435 | 32.7614 | 892.5379
9000.0062 | 27.2458 | 32.7903 | 893.4006
9015.0062 | 27.2446 | 32.732 | 891.7701
9030.0062 | 27.2468 | 32.7566 | 892.5125
9045.0062 | 27.248 | 32.7815 | 893.2283
9060.0062 | 27.2481 | 32.7516 | 892.4194
9075.0062 | 27.2521 | 32.6671 | 890.2466
9090.0062 | 27.2504 | 32.7671 | 892.9156
9105.0062 | 27.2518 | 32.6514 | 889.8091
9120.0062 | 27.2533 | 32.8119 | 894.2333
9135.0062 | 27.2559 | 32.8031 | 894.0778
9150.0062 | 27.2544 | 32.7758 | 893.2848
9165.0062 | 27.2566 | 32.793 | 893.8237
9180.0062 | 27.1026 | 27.4792 | 744.7555
9195.0062 | 27.2534 | 32.8031 | 893.9974
9210.0062 | 27.2578 | 32.7864 | 893.6848
9225.0062 | 27.2594 | 32.7185 | 891.8867
9240.0062 | 27.2632 | 32.7652 | 893.2828
9255.0062 | 27.2615 | 32.7837 | 893.7343
9270.0062 | 27.2639 | 32.6991 | 891.5063
9285.0062 | 27.2642 | 32.7674 | 893.3776
9300.0062 | 27.2664 | 32.6871 | 891.2598
9315.0062 | 27.2674 | 32.7777 | 893.7643
9330.0062 | 27.2669 | 32.7647 | 893.3896
9345.0062 | 27.2695 | 32.7245 | 892.381
9360.0062 | 27.271 | 32.7703 | 893.6777
9375.0062 | 27.2715 | 32.7385 | 892.829
9390.0062 | 27.274 | 32.7033 | 891.9499
9405.0062 | 27.274 | 32.7039 | 891.9649
9420.0062 | 27.2747 | 32.7584 | 893.4758
9435.0062 | 27.2755 | 32.7734 | 893.9101
9450.0062 | 27.2758 | 32.6534 | 890.6477
9465.0062 | 27.2798 | 32.7742 | 894.0721
9480.0062 | 27.2797 | 32.7135 | 892.414
9495.0062 | 27.2801 | 32.741 | 893.1781
9510.0062 | 27.281 | 32.7691 | 893.9741
9525.0062 | 27.2814 | 32.6734 | 891.3757
9540.0062 | 27.2826 | 32.7354 | 893.1045
9555.0062 | 27.2825 | 32.8114 | 895.1792
9570.0062 | 27.2812 | 32.7301 | 892.9166
9585.0062 | 27.2842 | 32.7233 | 892.8293
9600.0062 | 27.2869 | 32.7165 | 892.7306
9615.0062 | 27.2879 | 32.6635 | 891.3182
9630.0062 | 27.2896 | 32.6538 | 891.1089
9645.0062 | 27.2894 | 32.7257 | 893.0624
9660.0062 | 27.2904 | 32.6783 | 891.8042
9675.0062 | 27.2913 | 32.6495 | 891.0454
9690.0062 | 27.2926 | 32.7777 | 894.5868
9705.0062 | 27.2947 | 32.6855 | 892.1435
9720.0062 | 27.2935 | 32.6795 | 891.9407
9735.0062 | 27.2949 | 32.7132 | 892.9043
9750.0062 | 27.2958 | 32.7179 | 893.0626
9765.0062 | 27.296 | 32.7879 | 894.9782
9780.0063 | 27.1306 | 29.6313 | 803.9146
9795.0062 | 27.1442 | 28.9911 | 786.9385
9810.0062 | 27.2964 | 32.7444 | 893.8061
9825.0062 | 27.2976 | 32.7305 | 893.4649
9840.0062 | 27.3001 | 32.7169 | 893.1775
9855.0062 | 27.3018 | 32.6899 | 892.494
9870.0062 | 27.3025 | 32.726 | 893.5011
9885.0062 | 27.3038 | 32.7162 | 893.2763
9900.0062 | 27.3056 | 32.674 | 892.1828
9915.0062 | 27.3061 | 32.662 | 891.8725
9930.0062 | 27.3086 | 32.6315 | 891.1228
9945.0062 | 27.3082 | 32.6227 | 890.865
9960.0062 | 27.3086 | 32.6527 | 891.6993
9975.0062 | 27.31 | 32.6495 | 891.6581
9990.0062 | 27.3113 | 32.5942 | 890.1918
10005.0062 | 27.3087 | 32.7011 | 893.0267
10020.0062 | 27.3134 | 32.6917 | 892.9231
10035.0062 | 27.3134 | 32.7067 | 893.3333
10050.0062 | 27.3145 | 32.6854 | 892.7842
10065.0062 | 27.3145 | 32.6877 | 892.848
10080.0062 | 27.3173 | 32.6466 | 891.8157
10095.0062 | 27.3164 | 32.7652 | 895.0258
10110.0062 | 27.3191 | 32.6371 | 891.6188
10125.0062 | 27.3183 | 32.6478 | 891.8814
10140.0062 | 27.3187 | 32.6936 | 893.1477
10155.0062 | 27.3211 | 32.6973 | 893.3244
10170.0062 | 27.3232 | 32.7469 | 894.7515
10185.0062 | 27.3212 | 32.6819 | 892.9077
10200.0062 | 27.3204 | 32.7057 | 893.5332
10215.0062 | 27.3238 | 32.6869 | 893.128
10230.0062 | 27.3235 | 32.6139 | 891.1262
10245.0062 | 27.3248 | 32.6778 | 892.9132
10260.0062 | 27.3252 | 32.6949 | 893.3938
10275.0062 | 27.326 | 32.6115 | 891.1397
10290.0062 | 27.3261 | 32.7026 | 893.6327
10305.0062 | 27.3268 | 32.6192 | 891.3775
10320.0062 | 27.3292 | 32.7289 | 894.4553
10335.0062 | 27.3293 | 32.714 | 894.0495
10350.0062 | 27.3317 | 32.7073 | 893.9439
10365.0062 | 27.3306 | 32.6304 | 891.8069
10380.0062 | 27.1829 | 28.5201 | 775.2581
10395.0062 | 27.3261 | 32.6978 | 893.5021
10410.0062 | 27.3302 | 32.6294 | 891.7674
10425.0062 | 27.3312 | 32.7199 | 894.2752
10440.0062 | 27.3326 | 32.6428 | 892.2118
10455.0062 | 27.3339 | 32.6849 | 893.4065
10470.0062 | 27.3351 | 32.6231 | 891.7546
10485.0062 | 27.3375 | 32.6803 | 893.3989
10500.0062 | 27.3364 | 32.7131 | 894.2592
10515.0062 | 27.3404 | 32.7337 | 894.9518
10530.0062 | 27.339 | 32.7065 | 894.1652
10545.0062 | 27.3399 | 32.621 | 891.8535
10560.0062 | 27.3392 | 32.658 | 892.844
10575.0062 | 27.3411 | 32.6313 | 892.1775
10590.0062 | 27.3429 | 32.6137 | 891.7541
10605.0062 | 27.3448 | 32.6307 | 892.2812
10620.0062 | 27.3457 | 32.6478 | 892.7762
10635.0062 | 27.3466 | 32.6488 | 892.8332
10650.0062 | 27.3472 | 32.6785 | 893.6646
10665.0062 | 27.3472 | 32.6496 | 892.8774
10680.0062 | 27.3479 | 32.6768 | 893.6418
10695.0062 | 27.3497 | 32.6084 | 891.8292
10710.0062 | 27.3506 | 32.461 | 887.8289
10725.0062 | 27.3517 | 32.6608 | 893.3307
10740.0062 | 27.3531 | 32.6286 | 892.4908
10755.0062 | 27.3548 | 32.6111 | 892.0694
10770.0062 | 27.354 | 32.6616 | 893.4255
10785.0062 | 27.3541 | 32.6674 | 893.5876
10800.0062 | 27.3568 | 32.5769 | 891.1991
10815.0062 | 27.3575 | 32.6347 | 892.8013
10830.0062 | 27.3573 | 32.6472 | 893.1392
10845.0062 | 27.3586 | 32.5721 | 891.1278
10860.0062 | 27.3601 | 32.5342 | 890.1394
10875.0062 | 27.3593 | 32.6525 | 893.3487
10890.0062 | 27.3613 | 32.6178 | 892.4675
10905.0062 | 27.3627 | 32.6311 | 892.8733
10920.0062 | 27.3625 | 32.591 | 891.7734
10935.0062 | 27.3651 | 32.6275 | 892.8564
10950.0062 | 27.3648 | 32.5867 | 891.727
10965.0062 | 27.3642 | 32.6249 | 892.7557
10980.0062 | 27.1925 | 29.9072 | 813.253
10995.0062 | 27.3639 | 32.632 | 892.9384
11010.0062 | 27.3639 | 32.645 | 893.2938
11025.0062 | 27.3656 | 32.5989 | 892.09
11040.0062 | 27.3705 | 32.6889 | 894.7106
11055.0062 | 27.3694 | 32.626 | 892.9545
11070.0062 | 27.3697 | 32.6522 | 893.6804
11085.0062 | 27.3718 | 32.6543 | 893.8061
11100.0062 | 27.3732 | 32.5421 | 890.782
11115.0062 | 27.3753 | 32.6506 | 893.8188
11130.0062 | 27.3758 | 32.6255 | 893.1516
11145.0062 | 27.3738 | 32.5891 | 892.0859
11160.0062 | 27.3768 | 32.6224 | 893.0972
11175.0062 | 27.3779 | 32.6199 | 893.0637
11190.0062 | 27.3777 | 32.6752 | 894.5738
11205.0062 | 27.3799 | 32.6051 | 892.726
11220.0062 | 27.3833 | 32.5836 | 892.2471
11235.0062 | 27.382 | 32.5853 | 892.2503
11250.0062 | 27.383 | 32.5649 | 891.7242
11265.0062 | 27.3815 | 32.5756 | 891.9693
11280.0062 | 27.3835 | 32.5115 | 890.2784
11295.0062 | 27.3873 | 32.5886 | 892.5128
11310.0062 | 27.3857 | 32.6705 | 894.7048
11325.0062 | 27.3893 | 32.5715 | 892.1108
11340.0062 | 27.3898 | 32.6229 | 893.5338
11355.0062 | 27.39 | 32.504 | 890.2833
11370.0062 | 27.3896 | 32.6187 | 893.4131
11385.0062 | 27.3899 | 32.5772 | 892.2864
11400.0062 | 27.3916 | 32.608 | 893.1866
11415.0062 | 27.3935 | 32.5211 | 890.8656
11430.0062 | 27.3957 | 32.6125 | 893.441
11445.0062 | 27.3968 | 32.6141 | 893.5213
11460.0062 | 27.398 | 32.5982 | 893.1265
11475.0062 | 27.3976 | 32.6035 | 893.2591
11490.0062 | 27.3983 | 32.5625 | 892.1561
11505.0062 | 27.3985 | 32.5739 | 892.474
11520.0062 | 27.3995 | 32.5588 | 892.095
11535.0062 | 27.4003 | 32.6016 | 893.2959
11550.0062 | 27.4006 | 32.5164 | 890.9712
11565.0062 | 27.4029 | 32.6004 | 893.3449
11580.0062 | 27.2283 | 29.5665 | 805.0472
11595.0062 | 27.3995 | 32.5653 | 892.2741
11610.0062 | 27.4003 | 32.5612 | 892.1865
11625.0062 | 27.4042 | 32.6228 | 894.0012
11640.0062 | 27.4075 | 32.6178 | 893.9727
11655.0062 | 27.4072 | 32.5644 | 892.4995
11670.0062 | 27.4081 | 32.5862 | 893.1261
11685.0062 | 27.4102 | 32.5689 | 892.7183
11700.0062 | 27.4105 | 32.5323 | 891.7268
11715.0062 | 27.4123 | 32.632 | 894.5175
11730.0062 | 27.4126 | 32.5924 | 893.4441
11745.0062 | 27.414 | 32.5477 | 892.262
11760.0062 | 27.4141 | 32.5986 | 893.6618
11775.0062 | 27.4155 | 32.5316 | 891.8711
11790.0062 | 27.4161 | 32.6062 | 893.9336
11805.0062 | 27.4185 | 32.536 | 892.0881
11820.0062 | 27.4187 | 32.5313 | 891.9655
11835.0062 | 27.4199 | 32.5289 | 891.9409
11850.0062 | 27.4212 | 32.536 | 892.1766
11865.0062 | 27.4221 | 32.5366 | 892.2242
11880.0062 | 27.4218 | 32.5448 | 892.4381
11895.0062 | 27.4217 | 32.5388 | 892.2698
11910.0062 | 27.4234 | 32.5171 | 891.7292
11925.0062 | 27.4218 | 32.5812 | 893.4345
11940.0062 | 27.4245 | 32.5226 | 891.9174
11955.0062 | 27.4264 | 32.5175 | 891.8366
11970.0062 | 27.426 | 32.4956 | 891.2229
11985.0062 | 27.4274 | 32.6153 | 894.554
12000.0062 | 27.4294 | 32.5828 | 893.7259
12015.0062 | 27.4304 | 32.5557 | 893.0162
12030.0062 | 27.4288 | 32.6067 | 894.3631
12045.0062 | 27.4297 | 32.5688 | 893.3522
12060.0062 | 27.4318 | 32.5954 | 894.1513
12075.0062 | 27.43 | 32.5834 | 893.7635
12090.0062 | 27.4322 | 32.5376 | 892.5782
12105.0062 | 27.4331 | 32.5952 | 894.1849
12120.0062 | 27.435 | 32.5514 | 893.0468
12135.0062 | 27.4352 | 32.5548 | 893.1495
12150.0062 | 27.4332 | 32.6214 | 894.9083
12165.0062 | 27.4364 | 32.4735 | 890.9534
12180.0062 | 27.2938 | 26.8317 | 732.3381
12195.0062 | 27.3319 | 32.6217 | 891.6134
12210.0062 | 27.4332 | 32.566 | 893.3869
12225.0062 | 27.4361 | 32.6351 | 895.3811
12240.0062 | 27.4388 | 32.5907 | 894.2489
12255.0062 | 27.4379 | 32.5582 | 893.3289
12270.0062 | 27.4386 | 32.623 | 895.1293
12285.0062 | 27.4403 | 32.5115 | 892.1262
12300.0062 | 27.4425 | 32.5237 | 892.5327
12315.0062 | 27.4422 | 32.5323 | 892.7577
12330.0062 | 27.4423 | 32.4903 | 891.6102
12345.0062 | 27.4441 | 32.5613 | 893.6149
12360.0062 | 27.4467 | 32.5557 | 893.5464
12375.0062 | 27.4474 | 32.5857 | 894.3925
12390.0062 | 27.4466 | 32.6181 | 895.2557
12405.0062 | 27.4498 | 32.5314 | 892.9815
12420.0062 | 27.4495 | 32.5572 | 893.6789
12435.0062 | 27.4491 | 32.4722 | 891.3313
12450.0062 | 27.4506 | 32.5838 | 894.4456
12465.0062 | 27.4501 | 32.5271 | 892.8721
12480.0062 | 27.4503 | 32.5721 | 894.1156
12495.0062 | 27.4519 | 32.6015 | 894.974
12510.0062 | 27.4516 | 32.489 | 891.8731
12525.0062 | 27.4537 | 32.5054 | 892.3942
12540.0062 | 27.4531 | 32.5775 | 894.3542
12555.0062 | 27.455 | 32.5658 | 894.0942
12570.0062 | 27.4561 | 32.6238 | 895.7223
12585.0062 | 27.4564 | 32.5421 | 893.4861
12600.0062 | 27.4583 | 32.4766 | 891.7503
12615.0062 | 27.4577 | 32.5723 | 894.3613
12630.0062 | 27.4564 | 32.5219 | 892.9336
12645.0062 | 27.459 | 32.4677 | 891.5323
12660.0062 | 27.4589 | 32.4892 | 892.1184
12675.0062 | 27.4573 | 32.5176 | 892.8462
12690.0062 | 27.4586 | 32.5283 | 893.1828
12705.0062 | 27.4588 | 32.535 | 893.3706
12720.0062 | 27.4605 | 32.5663 | 894.2862
12735.0062 | 27.4589 | 32.5445 | 893.6386
12750.0062 | 27.4594 | 32.4424 | 890.8491
12765.0062 | 27.4614 | 32.5562 | 894.0384
12780.0062 | 27.3529 | 32.514 | 889.3529
12795.0062 | 27.459 | 32.5968 | 895.0769
12810.0062 | 27.4598 | 32.4835 | 891.9926
12825.0062 | 27.4631 | 32.5093 | 892.8071
12840.0062 | 27.4633 | 32.578 | 894.7001
12855.0062 | 27.4631 | 32.5295 | 893.3611
12870.0062 | 27.4654 | 32.5326 | 893.5224
12885.0062 | 27.4649 | 32.5484 | 893.9386
12900.0062 | 27.4651 | 32.5835 | 894.9111
12915.0062 | 27.4654 | 32.4776 | 892.0099
12930.0062 | 27.4666 | 32.5245 | 893.3356
12945.0062 | 27.4674 | 32.4718 | 891.9171
12960.0062 | 27.4677 | 32.4721 | 891.9338
12975.0062 | 27.4662 | 32.5003 | 892.657
12990.0062 | 27.4672 | 32.4923 | 892.4753
13005.0062 | 27.4684 | 32.4872 | 892.3717
13020.0062 | 27.4666 | 32.5486 | 894.0007
13035.0062 | 27.4665 | 32.5641 | 894.422
13050.0062 | 27.4688 | 32.5493 | 894.0901
13065.0062 | 27.472 | 32.5078 | 893.0539
13080.0062 | 27.471 | 32.561 | 894.4851
13095.0062 | 27.4713 | 32.5143 | 893.212
13110.0062 | 27.4722 | 32.4804 | 892.3089
13125.0062 | 27.4724 | 32.4944 | 892.6998
13140.0062 | 27.4723 | 32.467 | 891.9444
13155.0062 | 27.4724 | 32.5047 | 892.9832
13170.0062 | 27.4736 | 32.5115 | 893.2075
13185.0062 | 27.4728 | 32.5325 | 893.7582
13200.0062 | 27.4704 | 32.5389 | 893.8574
13215.0062 | 27.475 | 32.5598 | 894.5814
13230.0062 | 27.4734 | 32.5346 | 893.8351
13245.0062 | 27.4749 | 32.5289 | 893.728
13260.0062 | 27.473 | 32.5085 | 893.1062
13275.0062 | 27.4733 | 32.5261 | 893.5985
13290.0062 | 27.4741 | 32.4719 | 892.1343
13305.0062 | 27.4716 | 32.4583 | 891.6809
13320.0062 | 27.4742 | 32.4623 | 891.8745
13335.0062 | 27.4761 | 32.4506 | 891.6138
13350.0062 | 27.4767 | 32.5347 | 893.9447
13365.0062 | 27.4748 | 31.8911 | 876.2018
13380.0062 | 27.343 | 26.9145 | 735.9213
13395.0062 | 27.4733 | 32.4409 | 891.2582
13410.0062 | 27.4737 | 32.4544 | 891.6442
13425.0062 | 27.4761 | 32.4815 | 892.466
13440.0062 | 27.4782 | 32.5098 | 893.3122
13455.0062 | 27.4767 | 32.4607 | 891.9134
13470.0062 | 27.4791 | 32.5168 | 893.5308
13485.0062 | 27.4778 | 32.4835 | 892.5762
13500.0062 | 27.4782 | 32.5181 | 893.5368
13515.0062 | 27.4793 | 32.524 | 893.7369
13530.0062 | 27.4804 | 32.5456 | 894.366
13545.0062 | 27.4802 | 32.5609 | 894.7794
13560.0062 | 27.4798 | 32.451 | 891.7481
13575.0062 | 27.4824 | 32.493 | 892.9847
13590.0062 | 27.4805 | 32.4173 | 890.8438
13605.0062 | 27.4799 | 32.4741 | 892.3853
13620.0062 | 27.4823 | 32.4724 | 892.4168
13635.0062 | 27.4828 | 32.5276 | 893.9499
13650.0062 | 27.4837 | 32.5328 | 894.12
13665.0062 | 27.4804 | 32.4762 | 892.4585
13680.0062 | 27.4842 | 32.5243 | 893.9062
13695.0062 | 27.4829 | 32.4211 | 891.0257
13710.0062 | 27.4834 | 32.467 | 892.3046
13725.0062 | 27.4841 | 32.4955 | 893.1096
13740.0062 | 27.4827 | 32.4181 | 890.9351
13755.0062 | 27.4834 | 32.4669 | 892.3003
13770.0062 | 27.4843 | 32.4188 | 891.0076
13785.0062 | 27.4832 | 32.426 | 891.1698
13800.0062 | 27.4824 | 32.4782 | 892.5806
13815.0062 | 27.484 | 32.3972 | 890.4049
13830.0062 | 27.4847 | 32.4304 | 891.3381
13845.0062 | 27.4844 | 32.4831 | 892.7794
13860.0062 | 27.4822 | 32.5494 | 894.531
13875.0062 | 27.4848 | 32.3851 | 890.0986
13890.0062 | 27.4829 | 32.4507 | 891.8415
13905.0062 | 27.4858 | 32.5197 | 893.831
13920.0062 | 27.4839 | 32.4632 | 892.2172
13935.0062 | 27.4826 | 32.5204 | 893.7437
13950.0062 | 27.4832 | 32.4525 | 891.8962
13965.0062 | 27.4849 | 32.4219 | 891.1118
13980.0062 | 27.4093 | 27.5969 | 756.4102
13995.0062 | 27.484 | 32.4641 | 892.2437
14010.0062 | 27.4834 | 32.5763 | 895.3079
14025.0062 | 27.4861 | 32.4683 | 892.4265
14040.0062 | 27.484 | 32.5493 | 894.5837
14055.0062 | 27.4863 | 32.457 | 892.1234
14070.0062 | 27.4869 | 32.4839 | 892.8815
14085.0062 | 27.486 | 32.5001 | 893.2979
14100.0062 | 27.487 | 32.5307 | 894.1723
14115.0062 | 27.4884 | 32.461 | 892.3033
14130.0062 | 27.488 | 32.4933 | 893.1761
14145.0062 | 27.4885 | 32.5379 | 894.4191
14160.0062 | 27.4884 | 32.5107 | 893.6667
14175.0062 | 27.4902 | 32.5333 | 894.348
14190.0062 | 27.4887 | 32.456 | 892.1715
14205.0062 | 27.4878 | 32.4617 | 892.3003
14220.0062 | 27.4883 | 32.4548 | 892.1263
14235.0062 | 27.4901 | 32.5073 | 893.6301
14250.0062 | 27.4901 | 32.5046 | 893.5529
14265.0062 | 27.489 | 32.5107 | 893.6851
14280.0062 | 27.4911 | 32.5128 | 893.8124
14295.0062 | 27.4879 | 32.4791 | 892.7834
14310.0062 | 27.4894 | 32.4517 | 892.0783
14325.0062 | 27.4894 | 32.5098 | 893.674
14340.0062 | 27.4886 | 32.546 | 894.6447
14355.0062 | 27.4894 | 32.5052 | 893.5487
14370.0062 | 27.4886 | 32.5218 | 893.978
14385.0062 | 27.4891 | 32.5408 | 894.5184
14400.0062 | 27.4896 | 32.4691 | 892.5614
14415.0062 | 27.4922 | 32.3933 | 890.5657
14430.0062 | 27.4892 | 32.4731 | 892.6599
14445.0062 | 27.4904 | 32.5072 | 893.6349
14460.0062 | 27.4913 | 32.5569 | 895.0321
14475.0062 | 27.491 | 32.4896 | 893.171
14490.0062 | 27.491 | 32.4883 | 893.1374
14505.0062 | 27.491 | 32.4826 | 892.9768
14520.0062 | 27.4904 | 32.4559 | 892.2246
14535.0062 | 27.4912 | 32.4057 | 890.8708
14550.0062 | 27.4907 | 32.4663 | 892.5199
14565.0062 | 27.4921 | 32.3597 | 889.6334
14580.0062 | 27.4084 | 27.4842 | 753.2988
14595.0062 | 27.4847 | 32.5434 | 894.448
14610.0062 | 27.4888 | 32.5269 | 894.1254
14625.0062 | 27.4899 | 32.4816 | 892.9153
14640.0062 | 27.4898 | 32.4834 | 892.9621
14655.0062 | 27.4906 | 32.4684 | 892.577
14670.0062 | 27.4908 | 32.5255 | 894.1539
14685.0062 | 27.4925 | 32.4254 | 891.4548
14700.0062 | 27.4905 | 32.5038 | 893.5461
14715.0062 | 27.4894 | 32.4708 | 892.6006
14730.0062 | 27.4913 | 32.4947 | 893.3196
14745.0062 | 27.491 | 32.5451 | 894.6977
14760.0062 | 27.4907 | 32.5159 | 893.8855
14775.0062 | 27.4927 | 32.4586 | 892.3774
14790.0062 | 27.4927 | 32.4567 | 892.3226
14805.0062 | 27.4922 | 32.5024 | 893.5615
14820.0062 | 27.4914 | 32.4502 | 892.1015
14835.0062 | 27.4934 | 32.4672 | 892.6326
14850.0062 | 27.4909 | 32.5085 | 893.6887
14865.0062 | 27.4923 | 32.4207 | 891.3196
14880.0062 | 27.4912 | 32.5025 | 893.5345
14895.0062 | 27.4911 | 32.4452 | 891.9542
14910.0062 | 27.4914 | 32.5053 | 893.6155
14925.0062 | 27.4919 | 32.4427 | 891.911
14940.0062 | 27.4928 | 32.4447 | 891.9958
14955.0062 | 27.4909 | 32.5207 | 894.0246
14970.0062 | 27.4908 | 32.459 | 892.3225
14985.0062 | 27.4914 | 32.4956 | 893.3488
15000.0062 | 27.4918 | 32.5162 | 893.9307
15015.0062 | 27.4913 | 32.4624 | 892.4359
15030.0062 | 27.4919 | 32.4555 | 892.2616
15045.0062 | 27.4923 | 32.4273 | 891.5014
15060.0062 | 27.4916 | 32.4377 | 891.7651
15075.0062 | 27.4918 | 32.4561 | 892.2755
15090.0062 | 27.4922 | 32.4712 | 892.7045
15105.0062 | 27.4926 | 32.4527 | 892.2076
15120.0062 | 27.4908 | 32.495 | 893.3135
15135.0062 | 27.4899 | 32.5139 | 893.8029
15150.0062 | 27.4907 | 32.4938 | 893.2776
15165.0062 | 27.4928 | 28.5651 | 785.3356
15180.0062 | 27.4136 | 27.7007 | 759.3758
15195.0062 | 27.4873 | 32.5006 | 893.3542
15210.0062 | 27.4894 | 32.4679 | 892.5247
15225.0062 | 27.4886 | 32.5287 | 894.169
15240.0062 | 27.4884 | 32.553 | 894.829
15255.0062 | 27.4904 | 32.487 | 893.082
15270.0062 | 27.4905 | 32.5072 | 893.64
15285.0062 | 27.4906 | 32.4519 | 892.122
15300.0062 | 27.4905 | 32.4175 | 891.1733
15315.0062 | 27.4887 | 32.5059 | 893.5447
15330.0062 | 27.4906 | 32.4562 | 892.2385
15345.0062 | 27.4921 | 32.443 | 891.9269
15360.0062 | 27.4904 | 32.456 | 892.2288
15375.0062 | 27.491 | 32.5056 | 893.6098
15390.0062 | 27.4913 | 32.5036 | 893.5665
15405.0062 | 27.491 | 32.4671 | 892.5544
15420.0062 | 27.4894 | 32.5151 | 893.8196
15435.0062 | 27.4909 | 32.4978 | 893.3957
15450.0062 | 27.4905 | 32.4504 | 892.0777
15465.0062 | 27.4901 | 32.5091 | 893.6778
15480.0062 | 27.4913 | 32.4835 | 893.0139
15495.0062 | 27.4917 | 32.4159 | 891.1689
15510.0062 | 27.4907 | 32.4783 | 892.8517
15525.0062 | 27.4916 | 32.5022 | 893.5395
15540.0062 | 27.4908 | 32.4568 | 892.2633
15555.0062 | 27.4902 | 32.5039 | 893.5359
15570.0062 | 27.4896 | 32.4765 | 892.7662
15585.0062 | 27.4897 | 32.4998 | 893.408
15600.0062 | 27.4917 | 32.4908 | 893.2256
15615.0062 | 27.4898 | 32.4757 | 892.7506
15630.0062 | 27.4925 | 32.4057 | 890.9138
15645.0062 | 27.4908 | 32.4868 | 893.087
15660.0062 | 27.4918 | 32.5267 | 894.2153
15675.0062 | 27.4904 | 32.5369 | 894.4513
15690.0062 | 27.4886 | 32.4701 | 892.5578
15705.0062 | 27.4899 | 32.4095 | 890.9352
15720.0062 | 27.4897 | 32.5196 | 893.9562
15735.0062 | 27.4912 | 32.4576 | 892.2993
15750.0062 | 27.4893 | 32.4558 | 892.1859
15765.0062 | 27.4905 | 26.8567 | 738.306
15780.0062 | 27.3983 | 27.0012 | 739.7872
15795.0062 | 27.4869 | 32.4872 | 892.9723
15810.0062 | 27.4888 | 32.449 | 891.9846
15825.0062 | 27.4902 | 32.5099 | 893.703
15840.0062 | 27.4911 | 32.4535 | 892.1833
15855.0062 | 27.4912 | 32.3831 | 890.2497
15870.0062 | 27.4908 | 32.3921 | 890.4854
15885.0062 | 27.4922 | 32.4449 | 891.9808
15900.0062 | 27.4919 | 32.5402 | 894.5922
15915.0062 | 27.492 | 32.519 | 894.0132
15930.0062 | 27.4901 | 32.4688 | 892.5725
15945.0062 | 27.4925 | 32.4418 | 891.9067
15960.0062 | 27.4913 | 32.4613 | 892.4045
15975.0062 | 27.4909 | 32.5398 | 894.5482
15990.0062 | 27.4935 | 32.5182 | 894.0366
16005.0062 | 27.4918 | 32.4271 | 891.4773
16020.0062 | 27.492 | 32.4425 | 891.9095
16035.0062 | 27.4921 | 32.4734 | 892.7632
16050.0062 | 27.4926 | 32.493 | 893.3166
16065.0062 | 27.4928 | 32.4368 | 891.778
16080.0062 | 27.4923 | 32.4746 | 892.8032
16095.0062 | 27.4931 | 32.4745 | 892.8249
16110.0062 | 27.4909 | 32.4326 | 891.6029
16125.0062 | 27.4929 | 32.4228 | 891.3951
16140.0062 | 27.4934 | 32.5209 | 894.1092
16155.0062 | 27.4918 | 32.5141 | 893.8719
16170.0062 | 27.4911 | 32.4551 | 892.2258
16185.0062 | 27.4916 | 32.4454 | 891.9744
16200.0062 | 27.4919 | 32.4837 | 893.038
16215.0062 | 27.4929 | 32.4602 | 892.4251
16230.0062 | 27.4922 | 32.4689 | 892.6404
16245.0062 | 27.4914 | 32.4695 | 892.6312
16260.0062 | 27.4911 | 32.5394 | 894.5439
16275.0062 | 27.492 | 32.4873 | 893.141
16290.0062 | 27.4917 | 32.4601 | 892.3823
16305.0062 | 27.4905 | 32.4708 | 892.638
16320.0062 | 27.4912 | 32.48 | 892.9151
16335.0062 | 27.4936 | 32.5006 | 893.5595
16350.0062 | 27.4907 | 32.4781 | 892.8444
16365.0062 | 27.4902 | 26.8141 | 737.1256
16380.0062 | 27.4867 | 32.5012 | 893.3517
16395.0062 | 27.4889 | 32.4517 | 892.0613
16410.0062 | 27.4892 | 32.4876 | 893.0587
16425.0062 | 27.492 | 32.5532 | 894.9524
16440.0062 | 27.4902 | 32.4422 | 891.8417
16455.0062 | 27.4917 | 32.4867 | 893.1149
16470.0062 | 27.4925 | 32.4622 | 892.4651
16485.0062 | 27.4924 | 32.4657 | 892.5601
16500.0062 | 27.4906 | 32.4521 | 892.128
16515.0062 | 27.4925 | 32.4609 | 892.4315
16530.0062 | 27.4905 | 32.3955 | 890.5675
16545.0062 | 27.4928 | 32.4633 | 892.5086
16560.0062 | 27.4938 | 32.5161 | 893.991
16575.0062 | 27.4923 | 32.4832 | 893.037
16590.0062 | 27.4908 | 32.4931 | 893.2614
16605.0062 | 27.4915 | 32.4864 | 893.099
16620.0062 | 27.4918 | 32.5094 | 893.7408
16635.0062 | 27.49 | 32.502 | 893.4811
16650.0062 | 27.491 | 32.4109 | 891.0083
16665.0062 | 27.4927 | 32.4747 | 892.8178
16680.0062 | 27.4909 | 32.4916 | 893.2224
16695.0062 | 27.4911 | 32.4163 | 891.1578
16710.0062 | 27.4912 | 32.5058 | 893.6226
16725.0062 | 27.4902 | 32.4428 | 891.8601
16740.0062 | 27.4914 | 32.4927 | 893.2695
16755.0062 | 27.4904 | 32.4791 | 892.8622
16770.0062 | 27.492 | 32.4706 | 892.6825
16785.0062 | 27.4905 | 32.397 | 890.6113
16800.0062 | 27.4913 | 32.4581 | 892.3159
16815.0062 | 27.4929 | 32.5138 | 893.8988
16830.0062 | 27.4893 | 32.5606 | 895.0668
16845.0062 | 27.4908 | 32.4473 | 892.0001
16860.0062 | 27.4917 | 32.4812 | 892.965
16875.0062 | 27.4898 | 32.4466 | 891.9519
16890.0062 | 27.4921 | 32.4127 | 891.0922
16905.0062 | 27.4911 | 32.3437 | 889.1634
16920.0062 | 27.4903 | 32.5031 | 893.5188
16935.0062 | 27.4927 | 32.4818 | 893.0124
16950.0062 | 27.4924 | 32.4958 | 893.3861
16965.0062 | 27.4926 | 26.3077 | 723.2654
16980.0062 | 27.4881 | 32.4981 | 893.3112
16995.0062 | 27.4915 | 32.4484 | 892.054
17010.0062 | 27.4905 | 32.4508 | 892.0888
17025.0062 | 27.4914 | 32.4178 | 891.2117
17040.0062 | 27.4899 | 32.4978 | 893.36
17055.0062 | 27.4889 | 32.435 | 891.6036
17070.0062 | 27.4908 | 32.4465 | 891.9824
17085.0062 | 27.4914 | 32.5144 | 893.8669
17100.0062 | 27.4924 | 32.4831 | 893.0369
17115.0062 | 27.4907 | 32.4447 | 891.927
17130.0062 | 27.4914 | 32.4943 | 893.3144
17145.0062 | 27.4921 | 32.4633 | 892.4821
17160.0062 | 27.4903 | 32.5304 | 894.2715
17175.0062 | 27.4923 | 32.4747 | 892.8021
17190.0062 | 27.4924 | 32.4278 | 891.5168
17205.0062 | 27.4913 | 32.4978 | 893.4049
17220.0062 | 27.4927 | 32.5212 | 894.0969
17235.0062 | 27.4896 | 32.4769 | 892.7788
17250.0062 | 27.4908 | 32.4933 | 893.2661
17265.0062 | 27.4913 | 32.5159 | 893.9029
17280.0062 | 27.4914 | 32.4622 | 892.4331
17295.0062 | 27.4907 | 32.48 | 892.8963
17310.0062 | 27.4917 | 32.5328 | 894.3827
17325.0062 | 27.4908 | 32.5197 | 893.9942
17340.0062 | 27.4907 | 32.4579 | 892.2894
17355.0062 | 27.489 | 32.5458 | 894.6504
17370.0062 | 27.4904 | 32.4374 | 891.718
17385.0062 | 27.4915 | 32.4909 | 893.2244
17400.0062 | 27.4902 | 32.5358 | 894.4154
17415.0062 | 27.4916 | 32.439 | 891.7987
17430.0062 | 27.4896 | 32.4577 | 892.2497
17445.0062 | 27.4915 | 32.5032 | 893.5617
17460.0062 | 27.4903 | 32.5145 | 893.8341
17475.0062 | 27.4919 | 32.4815 | 892.9782
17490.0062 | 27.4913 | 32.518 | 893.9632
17505.0062 | 27.489 | 32.5078 | 893.6079
17520.0062 | 27.4894 | 32.4946 | 893.2556
17535.0062 | 27.4905 | 32.4562 | 892.238
17550.0062 | 27.4886 | 32.4936 | 893.202
17565.0062 | 27.4914 | 30.8894 | 849.1912
17580.0062 | 27.3362 | 27.7122 | 757.5461
17595.0062 | 27.4837 | 32.5322 | 894.1035
17610.0062 | 27.4865 | 32.4584 | 892.1677
17625.0062 | 27.488 | 32.5357 | 894.3409
17640.0062 | 27.4894 | 32.5744 | 895.4497
17655.0062 | 27.4899 | 32.5524 | 894.8616
17670.0062 | 27.4897 | 32.4868 | 893.0509
17685.0062 | 27.4908 | 32.5243 | 894.1182
17700.0062 | 27.4911 | 32.4137 | 891.0876
17715.0062 | 27.4912 | 32.4616 | 892.4087
17730.0062 | 27.4908 | 32.4279 | 891.4673
17745.0062 | 27.49 | 32.551 | 894.8265
17760.0062 | 27.4905 | 32.5158 | 893.8759
17775.0062 | 27.4901 | 32.4067 | 890.8638
17790.0062 | 27.4902 | 32.441 | 891.8115
17805.0062 | 27.4904 | 32.4846 | 893.0145
17820.0062 | 27.4902 | 32.4853 | 893.0275
17835.0062 | 27.491 | 32.4876 | 893.1154
17850.0062 | 27.4913 | 32.506 | 893.6315
17865.0062 | 27.4909 | 32.4117 | 891.0267
17880.0062 | 27.4894 | 32.4946 | 893.2589
17895.0062 | 27.4915 | 32.3956 | 890.6054
17910.0062 | 27.4899 | 32.5407 | 894.5414
17925.0062 | 27.4901 | 32.5001 | 893.4332
17940.0062 | 27.491 | 32.4349 | 891.668
17955.0062 | 27.4898 | 32.4249 | 891.3551
17970.0062 | 27.4919 | 32.5247 | 894.1667
17985.0062 | 27.4892 | 32.5164 | 893.8518
18000.0062 | 27.4908 | 32.5168 | 893.9126
18015.0062 | 27.4894 | 32.4962 | 893.3016
18030.0062 | 27.4904 | 32.3713 | 889.9017
18045.0062 | 27.4911 | 32.4406 | 891.8275
18060.0062 | 27.4898 | 32.5195 | 893.9531
18075.0062 | 27.4928 | 32.4738 | 892.7933
18090.0062 | 27.4896 | 32.4678 | 892.5259
18105.0062 | 27.4891 | 32.4784 | 892.8008
18120.0062 | 27.4901 | 32.4605 | 892.342
18135.0062 | 27.4887 | 32.4709 | 892.5834
18150.0062 | 27.4902 | 32.4925 | 893.2255
18165.0062 | 27.4903 | 30.6988 | 843.9208
18180.0062 | 27.3368 | 29.1744 | 797.5352
18195.0062 | 27.4876 | 32.5333 | 894.2606
18210.0062 | 27.4883 | 32.5429 | 894.5488
18225.0062 | 27.489 | 32.4876 | 893.0523
18240.0062 | 27.4888 | 32.5541 | 894.8716
18255.0062 | 27.4917 | 32.4709 | 892.681
18270.0062 | 27.4918 | 32.5414 | 894.6215
18285.0062 | 27.4911 | 32.4799 | 892.9068
18300.0062 | 27.4888 | 32.5122 | 893.7207
18315.0062 | 27.4894 | 32.5713 | 895.3664
18330.0062 | 27.4901 | 32.4707 | 892.6205
18345.0062 | 27.4902 | 32.4339 | 891.6131
18360.0062 | 27.4901 | 32.541 | 894.5555
18375.0062 | 27.4902 | 32.5103 | 893.7151
18390.0062 | 27.4928 | 32.4883 | 893.193
18405.0062 | 27.491 | 32.508 | 893.6774
18420.0062 | 27.4923 | 32.4161 | 891.1937
18435.0062 | 27.4919 | 32.4565 | 892.2908
18450.0062 | 27.4929 | 32.5152 | 893.9359
18465.0062 | 27.491 | 32.4177 | 891.1942
18480.0062 | 27.4897 | 32.5284 | 894.1967
18495.0062 | 27.4915 | 32.4752 | 892.7915
18510.0062 | 27.4903 | 32.5571 | 895.0056
18525.0062 | 27.4892 | 32.4604 | 892.3105
18540.0062 | 27.4921 | 32.4812 | 892.9772
18555.0062 | 27.492 | 32.4722 | 892.7258
18570.0062 | 27.4926 | 32.5053 | 893.6552
18585.0062 | 27.4903 | 32.4752 | 892.7531
18600.0062 | 27.4928 | 32.4821 | 893.0242
18615.0062 | 27.4912 | 32.5032 | 893.5501
18630.0062 | 27.4922 | 32.4933 | 893.3125
18645.0062 | 27.492 | 32.4638 | 892.4941
18660.0062 | 27.4923 | 32.4052 | 890.8939
18675.0062 | 27.4916 | 32.4971 | 893.3995
18690.0062 | 27.4939 | 32.4204 | 891.3622
18705.0062 | 27.4936 | 32.4907 | 893.2865
18720.0062 | 27.4898 | 32.4846 | 892.997
18735.0062 | 27.4915 | 32.5391 | 894.5486
18750.0062 | 27.4899 | 32.4604 | 892.3328
18765.0062 | 27.4791 | 26.5333 | 729.112
18780.0062 | 27.3371 | 29.2116 | 798.5603
18795.0062 | 27.4874 | 32.5302 | 894.1699
18810.0062 | 27.4888 | 32.5124 | 893.7273
18825.0062 | 27.4889 | 32.485 | 892.9769
18840.0062 | 27.4891 | 32.4287 | 891.4344
18855.0062 | 27.4911 | 32.3866 | 890.344
18870.0062 | 27.4911 | 32.4222 | 891.3203
18885.0062 | 27.4917 | 32.4731 | 892.7403
18900.0062 | 27.4908 | 32.5196 | 893.9889
18915.0062 | 27.4896 | 32.4817 | 892.9063
18930.0062 | 27.4899 | 32.474 | 892.7072
18945.0062 | 27.4884 | 32.4243 | 891.2918
18960.0062 | 27.4884 | 32.5373 | 894.3998
18975.0062 | 27.4896 | 32.5113 | 893.7244
18990.0062 | 27.4889 | 32.4712 | 892.5972
19005.0062 | 27.4895 | 32.4309 | 891.5088
19020.0062 | 27.4905 | 32.4463 | 891.9673
19035.0062 | 27.4903 | 32.4814 | 892.924
19050.0062 | 27.4908 | 32.4919 | 893.2271
19065.0062 | 27.4907 | 32.5138 | 893.828
19080.0062 | 27.4902 | 32.5095 | 893.6949
19095.0062 | 27.4889 | 32.4758 | 892.7256
19110.0062 | 27.4881 | 32.4848 | 892.9472
19125.0062 | 27.4907 | 32.508 | 893.6684
19140.0062 | 27.4912 | 32.5017 | 893.5118
19155.0062 | 27.4905 | 32.5231 | 894.0778
19170.0062 | 27.4909 | 32.4718 | 892.6776
19185.0062 | 27.4885 | 32.5164 | 893.8276
19200.0062 | 27.4914 | 32.4034 | 890.8156
19215.0062 | 27.4916 | 32.4602 | 892.3812
19230.0062 | 27.4919 | 32.4896 | 893.2014
19245.0062 | 27.4925 | 32.4667 | 892.5911
19260.0062 | 27.4905 | 32.5012 | 893.4739
19275.0062 | 27.4926 | 32.5218 | 894.1075
19290.0062 | 27.4924 | 32.5118 | 893.8277
19305.0062 | 27.4925 | 32.5167 | 893.9661
19320.0062 | 27.4932 | 32.4453 | 892.0243
19335.0062 | 27.4911 | 32.4893 | 893.169
19350.0062 | 27.4914 | 32.457 | 892.2862
19365.0062 | 27.49 | 29.878 | 821.3451
19380.0062 | 27.3528 | 29.3816 | 803.6686
19395.0062 | 27.4925 | 32.4205 | 891.3207
19410.0062 | 27.492 | 32.4374 | 891.7692
19425.0062 | 27.4934 | 32.4066 | 890.9663
19440.0062 | 27.4927 | 32.4657 | 892.5685
19455.0062 | 27.4924 | 32.4624 | 892.4711
19470.0062 | 27.4926 | 32.5074 | 893.7146
19485.0062 | 27.4912 | 32.4266 | 891.4475
19500.0062 | 27.4913 | 32.542 | 894.6212
19515.0062 | 27.4925 | 32.4499 | 892.1303
19530.0062 | 27.4942 | 32.5148 | 893.9685
19545.0062 | 27.4931 | 32.5643 | 895.2936
19560.0062 | 27.4932 | 32.4907 | 893.2739
19575.0062 | 27.4914 | 32.3878 | 890.3844
19590.0062 | 27.492 | 32.5034 | 893.5846
19605.0062 | 27.4936 | 32.4339 | 891.727
19620.0062 | 27.4918 | 32.5288 | 894.2755
19635.0062 | 27.4903 | 32.4821 | 892.9444
19650.0062 | 27.4903 | 32.4424 | 891.8498
19665.0062 | 27.493 | 32.5154 | 893.9468
19680.0062 | 27.4913 | 32.4749 | 892.7785
19695.0062 | 27.4922 | 32.4511 | 892.1536
19710.0062 | 27.4918 | 32.5009 | 893.5096
19725.0062 | 27.4906 | 32.4209 | 891.2691
19740.0062 | 27.491 | 32.4685 | 892.5903
19755.0062 | 27.4883 | 32.4654 | 892.4167
19770.0062 | 27.4914 | 32.5035 | 893.5679
19785.0062 | 27.4903 | 32.52 | 893.9835
19800.0062 | 27.4913 | 32.4695 | 892.6266
19815.0062 | 27.4908 | 32.5381 | 894.4989
19830.0062 | 27.4926 | 32.4844 | 893.0798
19845.0062 | 27.4913 | 32.5286 | 894.2532
19860.0062 | 27.4922 | 32.4613 | 892.4338
19875.0062 | 27.4907 | 32.4901 | 893.1756
19890.0062 | 27.4929 | 32.4946 | 893.3687
19905.0062 | 27.4917 | 32.4956 | 893.3602
19920.0062 | 27.4907 | 32.4965 | 893.3526
19935.0062 | 27.4918 | 32.4867 | 893.1175
19950.0062 | 27.4917 | 32.5188 | 893.9976
19965.0062 | 27.4871 | 29.2301 | 803.4499
19980.0062 | 27.3541 | 30.1908 | 825.8442
19995.0062 | 27.4873 | 32.4779 | 892.7284
20010.0062 | 27.4897 | 32.5057 | 893.5728
20025.0062 | 27.4894 | 32.5129 | 893.76
20040.0062 | 27.491 | 32.5142 | 893.8472
20055.0062 | 27.4888 | 32.4379 | 891.6792
20070.0062 | 27.4906 | 32.5348 | 894.3996
20085.0062 | 27.4913 | 32.535 | 894.4281
20100.0062 | 27.4914 | 32.5145 | 893.8688
20115.0062 | 27.4904 | 32.4442 | 891.9018
20130.0062 | 27.4902 | 32.4708 | 892.628
20145.0062 | 27.49 | 32.5072 | 893.6238
20160.0062 | 27.4881 | 32.4548 | 892.1219
20175.0062 | 27.4906 | 32.4865 | 893.0741
20190.0062 | 27.4915 | 32.4365 | 891.7264
20205.0062 | 27.4903 | 32.4434 | 891.8803
20220.0062 | 27.4921 | 32.3758 | 890.0773
20235.0062 | 27.4909 | 32.4387 | 891.7668
20250.0062 | 27.492 | 32.4385 | 891.7988
20265.0062 | 27.4937 | 32.4494 | 892.1543
20280.0062 | 27.4925 | 32.4176 | 891.2396
20295.0062 | 27.4938 | 32.504 | 893.6603
20310.0062 | 27.4929 | 32.355 | 889.5324
20325.0062 | 27.4917 | 32.4585 | 892.3416
20340.0062 | 27.4916 | 32.4807 | 892.9473
20355.0062 | 27.4907 | 32.4315 | 891.5647
20370.0062 | 27.4941 | 32.5184 | 894.0653
20385.0062 | 27.4929 | 32.4583 | 892.3723
20400.0062 | 27.4929 | 32.4527 | 892.2185
20415.0062 | 27.4932 | 32.361 | 889.7053
20430.0062 | 27.4929 | 32.4879 | 893.1853
20445.0062 | 27.4928 | 32.5265 | 894.2432
20460.0062 | 27.4917 | 32.4148 | 891.1394
20475.0062 | 27.4901 | 32.548 | 894.7486
20490.0062 | 27.4916 | 32.4119 | 891.0559
20505.0062 | 27.4912 | 32.4721 | 892.6972
20520.0062 | 27.4903 | 32.578 | 895.5813
20535.0062 | 27.4908 | 32.5045 | 893.5741
20550.0062 | 27.4901 | 32.5442 | 894.6447
20565.0062 | 27.3965 | 28.3416 | 776.4591
20580.0062 | 27.354 | 29.35 | 802.8389
20595.0062 | 27.4872 | 32.5311 | 894.1877
20610.0062 | 27.4879 | 32.5215 | 893.9487
20625.0062 | 27.4908 | 32.4327 | 891.5996
20640.0062 | 27.4908 | 32.496 | 893.3403
20655.0062 | 27.4894 | 32.4996 | 893.3945
20670.0062 | 27.4913 | 32.4875 | 893.1244
20685.0062 | 27.4907 | 32.544 | 894.6599
20700.0062 | 27.4921 | 32.4519 | 892.1715
20715.0062 | 27.4922 | 32.4431 | 891.9337
20730.0062 | 27.4907 | 32.4733 | 892.7124
20745.0062 | 27.4908 | 32.5269 | 894.1882
20760.0062 | 27.4904 | 32.4149 | 891.0991
20775.0062 | 27.4916 | 32.3762 | 890.0752
20790.0062 | 27.4919 | 32.4682 | 892.6145
20805.0062 | 27.4919 | 32.4242 | 891.4025
20820.0062 | 27.4916 | 32.4873 | 893.1281
20835.0062 | 27.4907 | 32.4613 | 892.3847
20850.0062 | 27.4929 | 32.5021 | 893.5765
20865.0062 | 27.4913 | 32.4671 | 892.5637
20880.0062 | 27.4913 | 32.4616 | 892.4113
20895.0062 | 27.4897 | 32.47 | 892.5914
20910.0062 | 27.4911 | 32.5237 | 894.114
20925.0062 | 27.4913 | 32.411 | 891.0205
20940.0062 | 27.4911 | 32.3919 | 890.487
20955.0062 | 27.4933 | 32.4694 | 892.6929
20970.0062 | 27.4944 | 32.3867 | 890.4527
20985.0062 | 27.4901 | 32.5108 | 893.7248
21000.0062 | 27.4939 | 32.5212 | 894.1361
21015.0062 | 27.4925 | 32.508 | 893.726
21030.0062 | 27.4905 | 32.5532 | 894.9047
21045.0062 | 27.4915 | 32.4292 | 891.5276
21060.0062 | 27.4923 | 32.4536 | 892.2232
21075.0062 | 27.4946 | 32.3967 | 890.7348
21090.0062 | 27.4911 | 32.4112 | 891.0197
21105.0062 | 27.4917 | 32.4087 | 890.97
21120.0062 | 27.4927 | 32.452 | 892.1918
21135.0062 | 27.4935 | 32.5399 | 894.6367
21150.0062 | 27.4948 | 32.3516 | 889.5027
21165.0062 | 27.4839 | 28.0452 | 770.7915
21180.0062 | 27.3382 | 32.5223 | 889.1027
21195.0062 | 27.4911 | 32.52 | 894.0118
21210.0062 | 27.4931 | 32.4573 | 892.3504
21225.0062 | 27.4906 | 32.4112 | 891.0054
21240.0062 | 27.4919 | 32.5282 | 894.261
21255.0062 | 27.4926 | 32.3829 | 890.2901
21270.0062 | 27.4931 | 32.4227 | 891.4012
21285.0062 | 27.4912 | 32.5012 | 893.496
21300.0062 | 27.4892 | 32.4388 | 891.7176
21315.0062 | 27.4931 | 32.4278 | 891.541
21330.0062 | 27.4929 | 32.5161 | 893.9606
21345.0062 | 27.4903 | 32.4547 | 892.1902
21360.0062 | 27.4912 | 32.4514 | 892.1275
21375.0062 | 27.4936 | 32.3666 | 889.875
21390.0062 | 27.4937 | 32.446 | 892.0594
21405.0062 | 27.4925 | 32.4343 | 891.6977
21420.0062 | 27.4914 | 32.512 | 893.8002
21435.0062 | 27.493 | 32.3401 | 889.1287
21450.0062 | 27.4921 | 32.5056 | 893.647
21465.0062 | 27.4942 | 32.4493 | 892.1691
21480.0062 | 27.4936 | 32.4444 | 892.0129
21495.0062 | 27.4907 | 32.4123 | 891.0352
21510.0062 | 27.4918 | 32.4276 | 891.4941
21525.0062 | 27.4904 | 32.4703 | 892.623
21540.0062 | 27.4907 | 32.428 | 891.4664
21555.0062 | 27.4909 | 32.4437 | 891.907
21570.0062 | 27.4941 | 32.4934 | 893.3781
21585.0062 | 27.4919 | 32.509 | 893.7338
21600.0062 | 27.4913 | 32.4744 | 892.7631
21615.0062 | 27.4921 | 32.4617 | 892.4396
21630.0062 | 27.4926 | 32.4837 | 893.059
21645.0062 | 27.4946 | 32.5592 | 895.2025
21660.0062 | 27.4926 | 32.4686 | 892.6452
21675.0062 | 27.4913 | 32.4561 | 892.2606
21690.0062 | 27.4931 | 32.457 | 892.3435
21705.0062 | 27.4915 | 32.4804 | 892.936
21720.0062 | 27.4901 | 32.5118 | 893.7517
21735.0062 | 27.4902 | 32.4219 | 891.2845
21750.0062 | 27.4929 | 32.4863 | 893.143
21765.0062 | 27.4771 | 27.5813 | 757.8524
21780.0062 | 27.3495 | 32.539 | 889.9233
21795.0062 | 27.4903 | 32.4939 | 893.2681
21810.0062 | 27.4905 | 32.3658 | 889.7532
21825.0062 | 27.4928 | 32.5095 | 893.7787
21840.0062 | 27.4924 | 32.425 | 891.4399
21855.0062 | 27.4937 | 32.4417 | 891.9416
21870.0062 | 27.4917 | 32.4338 | 891.6597
21885.0062 | 27.4929 | 32.4055 | 890.9188
21900.0062 | 27.4936 | 32.4402 | 891.8984
21915.0062 | 27.4934 | 32.4744 | 892.8305
21930.0062 | 27.4952 | 32.544 | 894.8024
21945.0062 | 27.4928 | 32.4746 | 892.8182
21960.0062 | 27.496 | 32.4844 | 893.1906
21975.0062 | 27.4959 | 32.5343 | 894.561
21990.0062 | 27.495 | 32.4874 | 893.2405
22005.0062 | 27.4947 | 32.5107 | 893.8715
22020.0062 | 27.4969 | 32.4606 | 892.5644
22035.0062 | 27.4932 | 32.5381 | 894.5744
22050.0062 | 27.4957 | 32.4991 | 893.5866
22065.0062 | 27.4954 | 32.4835 | 893.1452
22080.0062 | 27.4935 | 32.5169 | 894.0036
22095.0062 | 27.494 | 32.5198 | 894.099
22110.0062 | 27.493 | 32.5162 | 893.9665
22125.0062 | 27.4929 | 32.5093 | 893.7756
22140.0062 | 27.4953 | 32.4903 | 893.3301
22155.0062 | 27.4952 | 32.498 | 893.5379
22170.0062 | 27.4958 | 32.45 | 892.2395
22185.0062 | 27.4956 | 32.5258 | 894.3169
22200.0062 | 27.4934 | 32.5053 | 893.6796
22215.0062 | 27.4955 | 32.4666 | 892.687
22230.0062 | 27.4926 | 32.3945 | 890.6107
22245.0062 | 27.4924 | 32.4012 | 890.7868
22260.0062 | 27.4966 | 32.4689 | 892.7869
22275.0062 | 27.4914 | 32.4701 | 892.6494
22290.0062 | 27.4947 | 32.5094 | 893.8349
22305.0062 | 27.4957 | 32.4917 | 893.3828
22320.0062 | 27.4965 | 32.4483 | 892.2136
22335.0062 | 27.4948 | 32.4795 | 893.017
22350.0062 | 27.4958 | 32.4569 | 892.4304
22365.0062 | 27.3282 | 29.535 | 807.14
22380.0062 | 27.4922 | 32.4503 | 892.1325
22395.0062 | 27.4949 | 32.4855 | 893.1868
22410.0062 | 27.496 | 32.5223 | 894.234
22425.0062 | 27.4953 | 32.4701 | 892.7744
22440.0062 | 27.4957 | 32.4802 | 893.0643
22455.0062 | 27.495 | 32.505 | 893.7251
22470.0062 | 27.4925 | 32.4555 | 892.2842
22485.0062 | 27.4939 | 32.5464 | 894.8264
22500.0062 | 27.4955 | 32.5081 | 893.8259
22515.0062 | 27.4958 | 32.4693 | 892.7689
22530.0062 | 27.4965 | 32.4926 | 893.4324
22545.0062 | 27.495 | 32.5279 | 894.3553
22560.0062 | 27.4965 | 32.4985 | 893.5961
22575.0062 | 27.4979 | 32.4864 | 893.3104
22590.0062 | 27.4957 | 32.4586 | 892.4708
22605.0062 | 27.4947 | 32.5298 | 894.3956
22620.0062 | 27.4964 | 32.4907 | 893.3785
22635.0062 | 27.496 | 32.5308 | 894.4668
22650.0062 | 27.4958 | 32.5169 | 894.0779
22665.0062 | 27.498 | 32.4913 | 893.4443
22680.0062 | 27.4954 | 32.4805 | 893.0643
22695.0062 | 27.4952 | 32.4488 | 892.1871
22710.0062 | 27.4952 | 32.4836 | 893.143
22725.0062 | 27.4963 | 32.5271 | 894.3775
22740.0062 | 27.495 | 32.522 | 894.1919
22755.0062 | 27.4966 | 32.5605 | 895.305
22770.0062 | 27.4965 | 32.4754 | 892.959
22785.0062 | 27.4957 | 32.4309 | 891.7078
22800.0062 | 27.4954 | 32.5129 | 893.9569
22815.0062 | 27.4938 | 32.4965 | 893.4526
22830.0062 | 27.4965 | 32.473 | 892.8933
22845.0062 | 27.4956 | 32.4441 | 892.0689
22860.0062 | 27.4957 | 32.5512 | 895.0181
22875.0062 | 27.4965 | 32.4611 | 892.5666
22890.0062 | 27.4964 | 32.4839 | 893.1907
22905.0062 | 27.4963 | 32.5149 | 894.0405
22920.0062 | 27.4969 | 32.4697 | 892.8167
22935.0062 | 27.4954 | 32.4769 | 892.9652
22950.0062 | 27.4948 | 32.4951 | 893.4463
22965.0062 | 27.4636 | 26.7451 | 734.5169
22980.0062 | 27.3547 | 28.2464 | 772.6717
22995.0062 | 27.4906 | 32.4551 | 892.2091
23010.0062 | 27.4925 | 32.5354 | 894.4796
23025.0062 | 27.4942 | 32.4438 | 892.0148
23040.0062 | 27.4955 | 32.4681 | 892.7266
23055.0062 | 27.4956 | 32.456 | 892.3976
23070.0062 | 27.4969 | 32.489 | 893.3457
23085.0062 | 27.4972 | 32.4715 | 892.8733
23100.0062 | 27.4955 | 32.4848 | 893.1847
23115.0062 | 27.4956 | 32.5033 | 893.6962
23130.0062 | 27.4965 | 32.543 | 894.8175
23145.0062 | 27.4976 | 32.4779 | 893.0619
23160.0062 | 27.4967 | 32.49 | 893.3667
23175.0062 | 27.4954 | 32.4636 | 892.5973
23190.0062 | 27.4964 | 32.5189 | 894.1523
23205.0062 | 27.4968 | 32.4019 | 890.9466
23220.0062 | 27.4965 | 32.4416 | 892.0313
23235.0062 | 27.496 | 32.4544 | 892.3686
23250.0062 | 27.4962 | 32.4898 | 893.3451
23265.0062 | 27.4987 | 32.5217 | 894.305
23280.0062 | 27.496 | 32.4849 | 893.2031
23295.0062 | 27.4969 | 32.513 | 894.0061
23310.0062 | 27.4969 | 32.4633 | 892.6405
23325.0062 | 27.4947 | 32.4214 | 891.418
23340.0062 | 27.497 | 32.5124 | 893.9946
23355.0062 | 27.4973 | 32.4803 | 893.1191
23370.0062 | 27.4961 | 32.5423 | 894.7851
23385.0062 | 27.4981 | 32.5027 | 893.7627
23400.0062 | 27.4955 | 32.4834 | 893.147
23415.0062 | 27.4965 | 32.4811 | 893.116
23430.0062 | 27.4971 | 32.536 | 894.6443
23445.0062 | 27.4968 | 32.4192 | 891.4234
23460.0062 | 27.4979 | 32.4679 | 892.7985
23475.0062 | 27.4969 | 32.4891 | 893.3483
23490.0062 | 27.4969 | 32.5268 | 894.3853
23505.0062 | 27.4975 | 32.5185 | 894.1783
23520.0062 | 27.497 | 32.4838 | 893.2067
23535.0062 | 27.4961 | 32.4758 | 892.9585
23550.0062 | 27.4978 | 32.5623 | 895.3921
23565.0062 | 27.4564 | 26.6643 | 732.105
23580.0062 | 27.4087 | 32.5338 | 891.7079
23595.0062 | 27.4939 | 32.4475 | 892.1082
23610.0062 | 27.4948 | 32.4881 | 893.2514
23625.0062 | 27.4956 | 32.4646 | 892.6332
23640.0062 | 27.4986 | 32.4678 | 892.8196
23655.0062 | 27.4981 | 32.4638 | 892.6948
23670.0062 | 27.4978 | 32.4628 | 892.656
23685.0062 | 27.4954 | 32.4389 | 891.9224
23700.0062 | 27.4952 | 32.4601 | 892.4959
23715.0062 | 27.498 | 32.4493 | 892.2909
23730.0062 | 27.4972 | 32.4575 | 892.4885
23745.0062 | 27.4981 | 32.4255 | 891.639
23760.0062 | 27.4985 | 32.468 | 892.8224
23775.0062 | 27.4974 | 32.5225 | 894.2822
23790.0062 | 27.4974 | 32.484 | 893.226
23805.0062 | 27.4985 | 32.4771 | 893.071
23820.0062 | 27.4977 | 32.4829 | 893.2045
23835.0062 | 27.499 | 32.4704 | 892.9044
23850.0062 | 27.4986 | 32.485 | 893.2914
23865.0062 | 27.4981 | 32.4964 | 893.5883
23880.0062 | 27.4988 | 32.4907 | 893.4548
23895.0062 | 27.4983 | 32.4529 | 892.3997
23910.0062 | 27.499 | 32.4364 | 891.9691
23925.0062 | 27.4992 | 32.4142 | 891.366
23940.0062 | 27.4968 | 32.4349 | 891.8557
23955.0062 | 27.5 | 32.4196 | 891.5368
23970.0062 | 27.4982 | 32.4883 | 893.3705
23985.0062 | 27.5001 | 32.4126 | 891.3493
24000.0062 | 27.4995 | 32.4428 | 892.1607
24015.0062 | 27.4988 | 32.4645 | 892.7354
24030.0062 | 27.4999 | 32.43 | 891.8208
24045.0062 | 27.499 | 32.4455 | 892.2199
24060.0062 | 27.4989 | 32.4713 | 892.9266
24075.0062 | 27.4999 | 32.4639 | 892.7541
24090.0062 | 27.5002 | 32.4602 | 892.6611
24105.0062 | 27.4981 | 32.4661 | 892.7539
24120.0062 | 27.4985 | 32.5136 | 894.0757
24135.0062 | 27.4991 | 32.3972 | 890.8937
24150.0062 | 27.4985 | 32.4933 | 893.5172
24165.0062 | 27.4418 | 26.82 | 735.991
24180.0062 | 27.3669 | 27.1581 | 743.2335
24195.0062 | 27.494 | 32.4206 | 891.3717
24210.0062 | 27.4989 | 32.4117 | 891.2864
24225.0062 | 27.4998 | 32.4918 | 893.5183
24240.0062 | 27.4971 | 32.4325 | 891.8001
24255.0062 | 27.4986 | 32.4824 | 893.2231
24270.0062 | 27.4973 | 32.4677 | 892.7744
24285.0062 | 27.4998 | 32.5046 | 893.8721
24300.0062 | 27.5 | 32.4652 | 892.7938
24315.0062 | 27.5001 | 32.3898 | 890.7232
24330.0062 | 27.4993 | 32.4604 | 892.6401
24345.0062 | 27.4995 | 32.4545 | 892.4837
24360.0062 | 27.4995 | 32.4447 | 892.2144
24375.0062 | 27.4994 | 32.4666 | 892.8132
24390.0062 | 27.4997 | 32.4509 | 892.3918
24405.0062 | 27.5005 | 32.4339 | 891.947
24420.0062 | 27.5019 | 32.3879 | 890.7302
24435.0062 | 27.5018 | 32.4352 | 892.026
24450.0062 | 27.5064 | 32.4338 | 892.1386
24465.0062 | 27.507 | 32.4693 | 893.1315
24480.0062 | 27.5051 | 32.3338 | 889.3428
24495.0062 | 27.5062 | 32.4435 | 892.3979
24510.0062 | 27.5062 | 32.523 | 894.5839
24525.0062 | 27.5044 | 32.3983 | 891.0939
24540.0062 | 27.5059 | 32.3581 | 890.0368
24555.0062 | 27.5075 | 32.4449 | 892.4779
24570.0062 | 27.5053 | 32.4719 | 893.1522
24585.0062 | 27.5058 | 32.4565 | 892.7443
24600.0062 | 27.5057 | 32.4949 | 893.7949
24615.0062 | 27.5066 | 32.4693 | 893.1206
24630.0062 | 27.5037 | 32.4197 | 891.66
24645.0062 | 27.5049 | 32.4441 | 892.3693
24660.0062 | 27.5059 | 32.4581 | 892.7885
24675.0062 | 27.5072 | 32.4703 | 893.1657
24690.0062 | 27.5029 | 32.452 | 892.5259
24705.0062 | 27.5058 | 32.4087 | 891.4279
24720.0062 | 27.5044 | 32.4333 | 892.057
24735.0062 | 27.5052 | 32.4382 | 892.2209
24750.0062 | 27.5046 | 32.4291 | 891.9501
24765.0062 | 27.3407 | 27.2075 | 743.8729
24780.0062 | 27.4992 | 32.4673 | 892.8254
24795.0062 | 27.5025 | 32.5258 | 894.5406
24810.0062 | 27.5001 | 32.503 | 893.8362
24825.0062 | 27.5049 | 32.4496 | 892.5223
24840.0062 | 27.5022 | 32.4692 | 892.9725
24855.0062 | 27.5048 | 32.458 | 892.7499
24870.0062 | 27.5057 | 32.4687 | 893.0745
24885.0062 | 27.5068 | 32.4591 | 892.8468
24900.0062 | 27.5055 | 32.4563 | 892.7251
24915.0062 | 27.5048 | 32.4566 | 892.7098
24930.0062 | 27.5036 | 32.4603 | 892.7761
24945.0062 | 27.5035 | 32.5291 | 894.6635
24960.0062 | 27.5028 | 32.4863 | 893.4619
24975.0062 | 27.5056 | 32.4084 | 891.4122
24990.0062 | 27.5057 | 32.4826 | 893.4573
25005.0062 | 27.5067 | 32.3986 | 891.1796
25020.0062 | 27.5082 | 32.4518 | 892.6916
25035.0062 | 27.5056 | 32.4766 | 893.2908
25050.0062 | 27.5072 | 32.4689 | 893.1299
25065.0062 | 27.5073 | 32.4138 | 891.6165
25080.0062 | 27.5089 | 32.4994 | 894.0225
25095.0062 | 27.5081 | 32.4359 | 892.2518
25110.0062 | 27.5086 | 32.4436 | 892.4798
25125.0062 | 27.5076 | 32.49 | 893.722
25140.0062 | 27.5082 | 32.4497 | 892.6348
25155.0062 | 27.51 | 32.4586 | 892.9358
25170.0062 | 27.5088 | 32.4995 | 894.0223
25185.0062 | 27.5079 | 32.4565 | 892.8093
25200.0062 | 27.5079 | 32.5324 | 894.8968
25215.0062 | 27.5095 | 32.4974 | 893.9882
25230.0062 | 27.5095 | 32.404 | 891.4167
25245.0062 | 27.5083 | 32.5016 | 894.0631
25260.0062 | 27.5103 | 32.4856 | 893.6859
25275.0062 | 27.5095 | 32.444 | 892.5186
25290.0062 | 27.5091 | 32.4757 | 893.3785
25305.0062 | 27.5089 | 32.4834 | 893.5823
25320.0062 | 27.5088 | 32.4599 | 892.9326
25335.0062 | 27.508 | 32.4578 | 892.8482
25350.0062 | 27.5066 | 32.5291 | 894.7654
25365.0062 | 27.3627 | 26.9075 | 736.2609
25380.0062 | 27.4205 | 32.4727 | 890.4191
25395.0062 | 27.5064 | 32.4017 | 891.2536
25410.0062 | 27.5029 | 32.4124 | 891.4349
25425.0062 | 27.5085 | 32.498 | 893.9701
25440.0062 | 27.509 | 32.4832 | 893.5811
25455.0062 | 27.5073 | 32.405 | 891.3745
25470.0062 | 27.5089 | 32.486 | 893.6519
25485.0062 | 27.5095 | 32.4815 | 893.5505
25500.0062 | 27.5076 | 32.4943 | 893.8415
25515.0062 | 27.5098 | 32.482 | 893.5732
25530.0062 | 27.5079 | 32.4827 | 893.5295
25545.0062 | 27.5082 | 32.4505 | 892.6547
25560.0062 | 27.5095 | 32.4627 | 893.0335
25575.0062 | 27.5072 | 32.4816 | 893.4792
25590.0062 | 27.5103 | 32.4785 | 893.4951
25605.0062 | 27.5095 | 32.4442 | 892.5239
25620.0062 | 27.5094 | 32.493 | 893.8613
25635.0062 | 27.5093 | 32.4516 | 892.7219
25650.0062 | 27.5083 | 32.5294 | 894.8288
25665.0062 | 27.5088 | 32.4918 | 893.8102
25680.0062 | 27.5097 | 32.4884 | 893.7451
25695.0062 | 27.51 | 32.4054 | 891.4719
25710.0062 | 27.5088 | 32.4415 | 892.4258
25725.0062 | 27.5097 | 32.4748 | 893.3702
25740.0062 | 27.5104 | 32.4244 | 892.0053
25755.0062 | 27.5107 | 32.4482 | 892.6727
25770.0062 | 27.5105 | 32.4417 | 892.4874
25785.0062 | 27.5098 | 32.391 | 891.0672
25800.0062 | 27.5103 | 32.5002 | 894.0891
25815.0062 | 27.5084 | 32.4663 | 893.0961
25830.0062 | 27.5095 | 32.4921 | 893.8414
25845.0062 | 27.5106 | 32.4853 | 893.6927
25860.0062 | 27.5113 | 32.4835 | 893.6655
25875.0062 | 27.5099 | 32.4321 | 892.2042
25890.0062 | 27.5112 | 32.4873 | 893.7625
25905.0062 | 27.5115 | 32.3624 | 890.3356
25920.0062 | 27.51 | 32.4748 | 893.3819
25935.0062 | 27.5101 | 32.4978 | 894.0194
25950.0062 | 27.5111 | 32.435 | 892.3202
25965.0062 | 27.4199 | 27.6105 | 757.0769
25980.0062 | 27.4638 | 32.4239 | 890.4841
25995.0062 | 27.5094 | 32.5005 | 894.0697
26010.0062 | 27.5096 | 32.4951 | 893.9273
26025.0062 | 27.5125 | 32.4894 | 893.8658
26040.0062 | 27.5111 | 32.4907 | 893.8538
26055.0062 | 27.5105 | 32.4252 | 892.0336
26070.0062 | 27.5119 | 32.4932 | 893.9498
26085.0062 | 27.5113 | 32.4215 | 891.9564
26100.0062 | 27.5135 | 32.4449 | 892.6722
26115.0062 | 27.5119 | 32.458 | 892.9806
26130.0062 | 27.5111 | 32.4866 | 893.7414
26145.0062 | 27.5128 | 32.464 | 893.1745
26160.0062 | 27.5118 | 32.4661 | 893.2008
26175.0062 | 27.5103 | 32.3839 | 890.8897
26190.0062 | 27.5122 | 32.4731 | 893.4074
26205.0062 | 27.512 | 32.3542 | 890.129
26220.0062 | 27.5116 | 32.4529 | 892.8309
26235.0062 | 27.513 | 32.3942 | 891.2612
26250.0062 | 27.5112 | 32.5005 | 894.1264
26265.0062 | 27.5104 | 32.4388 | 892.4065
26280.0062 | 27.513 | 32.4885 | 893.8545
26295.0062 | 27.5145 | 32.4122 | 891.8057
26310.0062 | 27.5142 | 32.5115 | 894.5292
26325.0062 | 27.5135 | 32.477 | 893.5549
26340.0062 | 27.5133 | 32.4637 | 893.1835
26355.0062 | 27.5118 | 32.5043 | 894.252
26370.0062 | 27.5144 | 32.4256 | 892.172
26385.0062 | 27.5145 | 32.3926 | 891.2688
26400.0062 | 27.5129 | 32.4326 | 892.3132
26415.0062 | 27.5142 | 32.4255 | 892.1615
26430.0062 | 27.5142 | 32.4485 | 892.7931
26445.0062 | 27.514 | 32.434 | 892.3891
26460.0062 | 27.5139 | 32.4784 | 893.6078
26475.0062 | 27.5146 | 32.5151 | 894.64
26490.0062 | 27.5143 | 32.4335 | 892.3844
26505.0062 | 27.5154 | 32.4925 | 894.042
26520.0062 | 27.5142 | 32.4968 | 894.1224
26535.0062 | 27.5135 | 32.4566 | 892.9962
26550.0062 | 27.5137 | 32.4848 | 893.7765
26565.0062 | 27.422 | 27.0883 | 742.8152
26580.0062 | 27.5121 | 32.4293 | 892.1969
26595.0062 | 27.5122 | 32.4047 | 891.5242
26610.0062 | 27.5143 | 32.4191 | 891.9897
26625.0062 | 27.5133 | 32.4879 | 893.8509
26640.0062 | 27.515 | 32.5082 | 894.4635
26655.0062 | 27.514 | 32.4469 | 892.7448
26670.0062 | 27.5156 | 32.426 | 892.2198
26685.0062 | 27.5154 | 32.3691 | 890.6494
26700.0062 | 27.5162 | 32.4364 | 892.5273
26715.0062 | 27.5157 | 32.3972 | 891.4297
26730.0062 | 27.5146 | 32.4443 | 892.692
26745.0062 | 27.5142 | 32.4127 | 891.8109
26760.0062 | 27.516 | 32.3799 | 890.9674
26775.0062 | 27.5148 | 32.4247 | 892.1614
26790.0062 | 27.5156 | 32.5099 | 894.5298
26805.0062 | 27.5137 | 32.4824 | 893.7094
26820.0062 | 27.5156 | 32.4525 | 892.9496
26835.0062 | 27.5158 | 32.5454 | 895.5121
26850.0062 | 27.5173 | 32.4484 | 892.8908
26865.0062 | 27.5173 | 32.4582 | 893.163
26880.0062 | 27.5158 | 32.4883 | 893.9408
26895.0062 | 27.5165 | 32.417 | 892.0028
26910.0062 | 27.5163 | 32.5201 | 894.8307
26925.0062 | 27.5187 | 32.4605 | 893.2691
26940.0062 | 27.5177 | 32.4583 | 893.1779
26955.0062 | 27.5175 | 32.458 | 893.1648
26970.0062 | 27.5191 | 32.4746 | 893.6737
26985.0062 | 27.5179 | 32.3902 | 891.3101
27000.0062 | 27.518 | 32.4957 | 894.2168
27015.0062 | 27.5174 | 32.4374 | 892.5951
27030.0062 | 27.517 | 32.4674 | 893.4046
27045.0062 | 27.5186 | 32.5002 | 894.3599
27060.0062 | 27.519 | 32.4747 | 893.6721
27075.0062 | 27.518 | 32.4765 | 893.6909
27090.0062 | 27.5176 | 32.4517 | 892.9941
27105.0062 | 27.5194 | 32.4545 | 893.1279
27120.0062 | 27.52 | 32.4373 | 892.6752
27135.0062 | 27.5196 | 32.4432 | 892.8238
27150.0062 | 27.5197 | 32.432 | 892.5208
27165.0062 | 27.4434 | 27.6874 | 759.8351
27180.0062 | 27.4697 | 32.441 | 891.1435
27195.0062 | 27.5142 | 32.4915 | 893.9757
27210.0062 | 27.5178 | 32.4793 | 893.7573
27225.0062 | 27.5195 | 32.4932 | 894.1952
27240.0062 | 27.5204 | 32.4389 | 892.7296
27255.0062 | 27.5207 | 32.5089 | 894.6675
27270.0062 | 27.52 | 32.4702 | 893.578
27285.0062 | 27.52 | 32.4634 | 893.3915
27300.0062 | 27.5208 | 32.5317 | 895.2992
27315.0062 | 27.5211 | 32.4516 | 893.1031
27330.0062 | 27.5228 | 32.473 | 893.7472
27345.0062 | 27.5227 | 32.4139 | 892.1189
27360.0062 | 27.5235 | 32.4506 | 893.1534
27375.0062 | 27.5236 | 32.4005 | 891.7789
27390.0062 | 27.5238 | 32.4519 | 893.2003
27405.0062 | 27.5218 | 32.4398 | 892.8012
27420.0062 | 27.5235 | 32.4656 | 893.5676
27435.0062 | 27.5242 | 32.413 | 892.143
27450.0062 | 27.5225 | 32.4131 | 892.0906
27465.0062 | 27.5222 | 32.485 | 894.0595
27480.0062 | 27.5227 | 32.4258 | 892.4464
27495.0062 | 27.5227 | 32.4649 | 893.521
27510.0062 | 27.5235 | 32.4775 | 893.8967
27525.0062 | 27.5228 | 32.4642 | 893.5054
27540.0062 | 27.5221 | 32.4329 | 892.6218
27555.0062 | 27.5234 | 32.4267 | 892.4936
27570.0062 | 27.5233 | 32.4401 | 892.8609
27585.0062 | 27.5222 | 32.4912 | 894.2277
27600.0062 | 27.5242 | 32.4487 | 893.1239
27615.0062 | 27.5244 | 32.422 | 892.3953
27630.0062 | 27.5261 | 32.4753 | 893.9191
27645.0062 | 27.5246 | 32.4399 | 892.8971
27660.0062 | 27.5245 | 32.4078 | 892.007
27675.0062 | 27.5239 | 32.4743 | 893.8212
27690.0062 | 27.5237 | 32.4494 | 893.1279
27705.0062 | 27.5263 | 32.4181 | 892.3524
27720.0062 | 27.5238 | 32.4526 | 893.2177
27735.0062 | 27.5257 | 32.488 | 894.2542
27750.0062 | 27.5269 | 32.4282 | 892.6477
27765.0062 | 27.3753 | 25.8638 | 708.0294
27780.0062 | 27.4196 | 26.3399 | 722.2294
27795.0062 | 27.5231 | 32.3822 | 891.2587
27810.0062 | 27.5273 | 32.4655 | 893.6876
27825.0062 | 27.5266 | 32.4772 | 893.9859
27840.0062 | 27.5274 | 32.4498 | 893.2565
27855.0062 | 27.527 | 32.4287 | 892.6633
27870.0062 | 27.5265 | 32.5044 | 894.7335
27885.0062 | 27.5267 | 32.4502 | 893.2468
27900.0062 | 27.5285 | 32.4365 | 892.9293
27915.0062 | 27.5268 | 32.4676 | 893.7283
27930.0062 | 27.5268 | 32.4422 | 893.0297
27945.0062 | 27.5261 | 32.4429 | 893.0259
27960.0062 | 27.5258 | 32.433 | 892.7446
27975.0062 | 27.5278 | 32.5006 | 894.6692
27990.0062 | 27.5263 | 32.468 | 893.7254
28005.0062 | 27.5273 | 32.4933 | 894.4544
28020.0062 | 27.5277 | 32.4203 | 892.4554
28035.0062 | 27.5275 | 32.483 | 894.1749
28050.0062 | 27.528 | 32.4368 | 892.9211
28065.0062 | 27.5295 | 32.4537 | 893.4334
28080.0062 | 27.5274 | 32.4323 | 892.7748
28095.0062 | 27.5294 | 32.4531 | 893.4161
28110.0062 | 27.5283 | 32.4285 | 892.7009
28125.0062 | 27.5256 | 32.4252 | 892.5241
28140.0062 | 27.5297 | 32.4605 | 893.6279
28155.0062 | 27.5284 | 32.425 | 892.6083
28170.0062 | 27.5282 | 32.4502 | 893.2949
28185.0062 | 27.5297 | 32.436 | 892.9512
28200.0062 | 27.5279 | 32.4878 | 894.3217
28215.0062 | 27.5266 | 32.4786 | 894.0244
28230.0062 | 27.5294 | 32.4435 | 893.1479
28245.0062 | 27.5274 | 32.475 | 893.9503
28260.0062 | 27.5296 | 32.4638 | 893.7172
28275.0062 | 27.5296 | 32.456 | 893.5014
28290.0062 | 27.529 | 32.4947 | 894.5457
28305.0062 | 27.5309 | 32.4077 | 892.2123
28320.0062 | 27.5301 | 32.3864 | 891.6011
28335.0062 | 27.5312 | 32.499 | 894.7352
28350.0062 | 27.5305 | 32.3744 | 891.2835
28365.0062 | 27.3787 | 25.8776 | 708.4937
28380.0062 | 27.4215 | 26.1695 | 717.6057
28395.0062 | 27.5261 | 32.465 | 893.6352
28410.0062 | 27.53 | 32.4562 | 893.5203
28425.0062 | 27.5304 | 32.4467 | 893.2717
28440.0062 | 27.5313 | 32.4063 | 892.186
28455.0062 | 27.5316 | 32.4552 | 893.5431
28470.0062 | 27.5325 | 32.4576 | 893.6398
28485.0062 | 27.5314 | 32.4432 | 893.2083
28500.0062 | 27.5303 | 32.469 | 893.8823
28515.0062 | 27.5308 | 32.4489 | 893.3446
28530.0062 | 27.5319 | 32.4165 | 892.4894
28545.0062 | 27.5335 | 32.3835 | 891.6329
28560.0062 | 27.5332 | 32.4286 | 892.8625
28575.0062 | 27.5316 | 32.4313 | 892.8845
28590.0062 | 27.5354 | 32.3772 | 891.517
28605.0062 | 27.5318 | 32.4861 | 894.4008
28620.0062 | 27.5333 | 32.4444 | 893.3015
28635.0062 | 27.5335 | 32.4222 | 892.6943
28650.0062 | 27.5311 | 32.3845 | 891.582
28665.0062 | 27.5339 | 32.4973 | 894.7791
28680.0062 | 27.5348 | 32.4677 | 893.9909
28695.0062 | 27.5343 | 32.4699 | 894.0355
28710.0062 | 27.5368 | 32.4231 | 892.8306
28725.0062 | 27.5345 | 32.396 | 892.0077
28740.0062 | 27.5368 | 32.4353 | 893.1643
28755.0062 | 27.5367 | 32.4135 | 892.5585
28770.0062 | 27.5353 | 32.4686 | 894.0318
28785.0062 | 27.5375 | 32.4226 | 892.8388
28800.0062 | 27.5382 | 32.4135 | 892.6094
28815.0062 | 27.5362 | 32.4229 | 892.8044
28830.0062 | 27.5379 | 32.3985 | 892.1872
28845.0062 | 27.5366 | 32.3661 | 891.2515
28860.0062 | 27.538 | 32.3658 | 891.2887
28875.0062 | 27.5387 | 32.4244 | 892.9268
28890.0062 | 27.5394 | 32.4156 | 892.7083
28905.0062 | 27.5389 | 32.4521 | 893.694
28920.0062 | 27.5399 | 32.3366 | 890.5444
28935.0062 | 27.5377 | 32.4626 | 893.945
28950.0062 | 27.5381 | 32.2929 | 889.285
28965.0062 | 27.4128 | 26.0271 | 713.4762
28980.0062 | 27.5305 | 32.5045 | 894.8624
28995.0062 | 27.5349 | 32.4601 | 893.7863
29010.0062 | 27.5391 | 32.436 | 893.2572
29025.0062 | 27.5372 | 32.4605 | 893.8703
29040.0062 | 27.539 | 32.4313 | 893.1248
29055.0062 | 27.5389 | 32.4435 | 893.456
29070.0062 | 27.5389 | 32.4359 | 893.2512
29085.0062 | 27.5394 | 32.4342 | 893.2169
29100.0062 | 27.5424 | 32.4367 | 893.3845
29115.0062 | 27.5398 | 32.4112 | 892.597
29130.0062 | 27.5406 | 32.4588 | 893.9361
29145.0062 | 27.5408 | 32.4146 | 892.7232
29160.0062 | 27.541 | 32.4109 | 892.6283
29175.0062 | 27.5395 | 32.3726 | 891.5242
29190.0062 | 27.5437 | 32.4262 | 893.1363
29205.0062 | 27.541 | 32.4178 | 892.8199
29220.0062 | 27.5428 | 32.43 | 893.2131
29235.0062 | 27.5441 | 32.4075 | 892.6357
29250.0062 | 27.5408 | 32.3885 | 892.0039
29265.0062 | 27.5437 | 32.4199 | 892.9637
29280.0062 | 27.5436 | 32.4077 | 892.6256
29295.0062 | 27.5438 | 32.5013 | 895.207
29310.0062 | 27.5448 | 32.4352 | 893.4217
29325.0062 | 27.544 | 32.4342 | 893.3672
29340.0062 | 27.545 | 32.4343 | 893.4038
29355.0062 | 27.5448 | 32.4629 | 894.183
29370.0062 | 27.5446 | 32.4029 | 892.5241
29385.0062 | 27.5445 | 32.3579 | 891.2813
29400.0062 | 27.5456 | 32.4845 | 894.8056
29415.0062 | 27.5465 | 32.4149 | 892.9162
29430.0062 | 27.5447 | 32.4943 | 895.0458
29445.0062 | 27.5458 | 32.4474 | 893.7872
29460.0062 | 27.5476 | 32.4257 | 893.25
29475.0062 | 27.5474 | 32.3962 | 892.4291
29490.0062 | 27.5469 | 32.4394 | 893.604
29505.0062 | 27.548 | 32.4182 | 893.0569
29520.0062 | 27.5465 | 32.4306 | 893.3501
29535.0062 | 27.5489 | 32.4074 | 892.7874
29550.0062 | 27.5495 | 32.4082 | 892.8281
29565.0062 | 27.3976 | 27.9012 | 764.4257
29580.0062 | 27.3975 | 28.7863 | 788.6735
29595.0062 | 27.5454 | 32.4679 | 894.3405
29610.0062 | 27.5472 | 32.393 | 892.3341
29625.0062 | 27.55 | 32.4421 | 893.7814
29640.0062 | 27.5497 | 32.4274 | 893.3655
29655.0062 | 27.5503 | 32.4257 | 893.3374
29670.0062 | 27.55 | 32.4045 | 892.7435
29685.0062 | 27.5511 | 32.4352 | 893.6263
29700.0062 | 27.5492 | 32.458 | 894.1901
29715.0062 | 27.5531 | 32.4096 | 892.9862
29730.0062 | 27.5541 | 32.4587 | 894.3716
29745.0062 | 27.552 | 32.472 | 894.6699
29760.0062 | 27.5534 | 32.4606 | 894.3996
29775.0062 | 27.5531 | 32.4876 | 895.136
29790.0062 | 27.5533 | 32.4574 | 894.3086
29805.0062 | 27.5556 | 32.4329 | 893.7075
29820.0062 | 27.5541 | 32.3445 | 891.2231
29835.0062 | 27.5556 | 32.4596 | 894.4449
29850.0062 | 27.5536 | 32.4395 | 893.8242
29865.0062 | 27.5557 | 32.4229 | 893.4386
29880.0062 | 27.5553 | 32.3988 | 892.7561
29895.0062 | 27.5559 | 32.4083 | 893.0393
29910.0062 | 27.5559 | 32.425 | 893.4992
29925.0062 | 27.5565 | 32.3713 | 892.04
29940.0062 | 27.5563 | 32.3739 | 892.1056
29955.0062 | 27.5561 | 32.3926 | 892.6138
29970.0062 | 27.556 | 32.4262 | 893.5385
29985.0062 | 27.5579 | 32.37 | 892.0483
30000.0062 | 27.5587 | 32.4183 | 893.4045
30015.0062 | 27.5578 | 32.4108 | 893.1703
30030.0062 | 27.5586 | 32.3614 | 891.8356
30045.0062 | 27.5588 | 32.4217 | 893.5019
30060.0062 | 27.5571 | 32.4035 | 892.9471
30075.0062 | 27.5588 | 32.4087 | 893.145
30090.0062 | 27.561 | 32.4111 | 893.281
30105.0062 | 27.5602 | 32.436 | 893.9422
30120.0062 | 27.5607 | 32.3982 | 892.9163
30135.0062 | 27.5608 | 32.4621 | 894.6816
30150.0062 | 27.5627 | 32.3313 | 891.1387
30165.0062 | 27.4163 | 26.84 | 735.8517
30180.0062 | 27.556 | 32.4387 | 893.8788
30195.0062 | 27.5599 | 32.4154 | 893.3632
30210.0062 | 27.5619 | 32.3437 | 891.456
30225.0062 | 27.5621 | 32.4412 | 894.1477
30240.0062 | 27.5627 | 32.4078 | 893.2469
30255.0062 | 27.5657 | 32.408 | 893.3515
30270.0062 | 27.563 | 32.4146 | 893.4451
30285.0062 | 27.5649 | 32.4217 | 893.7025
30300.0062 | 27.5673 | 32.3935 | 893.0007
30315.0062 | 27.564 | 32.3396 | 891.4083
30330.0062 | 27.5665 | 32.3512 | 891.8083
30345.0062 | 27.5692 | 32.4353 | 894.2143
30360.0062 | 27.567 | 32.3681 | 892.2908
30375.0062 | 27.5685 | 32.2926 | 890.2604
30390.0062 | 27.5697 | 32.3751 | 892.5717
30405.0062 | 27.57 | 32.4516 | 894.6921
30420.0062 | 27.5696 | 32.3943 | 893.0958
30435.0062 | 27.5706 | 32.4039 | 893.3956
30450.0062 | 27.5699 | 32.4594 | 894.9027
30465.0062 | 27.571 | 32.4611 | 894.9854
30480.0062 | 27.5712 | 32.3975 | 893.2394
30495.0062 | 27.5726 | 32.4168 | 893.8143
30510.0062 | 27.5703 | 32.4272 | 894.026
30525.0062 | 27.574 | 32.4114 | 893.7131
30540.0062 | 27.5739 | 32.423 | 894.0276
30555.0062 | 27.5761 | 32.3262 | 891.4303
30570.0062 | 27.574 | 32.4232 | 894.0377
30585.0062 | 27.5746 | 32.4215 | 894.0102
30600.0062 | 27.5741 | 32.3715 | 892.614
30615.0062 | 27.5767 | 32.2943 | 890.5683
30630.0062 | 27.577 | 32.3662 | 892.563
30645.0062 | 27.5785 | 32.28 | 890.2334
30660.0062 | 27.577 | 32.3997 | 893.4847
30675.0062 | 27.5787 | 32.3791 | 892.9735
30690.0062 | 27.5798 | 32.4115 | 893.9025
30705.0062 | 27.5783 | 32.346 | 892.0467
30720.0062 | 27.5803 | 32.4453 | 894.8514
30735.0062 | 27.579 | 32.4396 | 894.6509
30750.0062 | 27.5806 | 32.367 | 892.6995
30765.0062 | 27.4512 | 27.4232 | 752.8006
30780.0062 | 27.4291 | 29.0474 | 796.7418
30795.0062 | 27.581 | 32.4043 | 893.7446
30810.0062 | 27.5814 | 32.3386 | 891.9439
30825.0062 | 27.5831 | 32.3855 | 893.2909
30840.0062 | 27.5838 | 32.28 | 890.4053
30855.0062 | 27.5827 | 32.3368 | 891.936
30870.0062 | 27.585 | 32.3654 | 892.7996
30885.0062 | 27.5847 | 32.3883 | 893.4206
30900.0062 | 27.5869 | 32.3198 | 891.6043
30915.0062 | 27.5844 | 32.4112 | 894.0432
30930.0062 | 27.589 | 32.4534 | 895.3591
30945.0062 | 27.5864 | 32.4088 | 894.0428
30960.0062 | 27.5889 | 32.2968 | 891.0336
30975.0062 | 27.5917 | 32.3916 | 893.7384
30990.0062 | 27.5904 | 32.398 | 893.8755
31005.0062 | 27.5923 | 32.3092 | 891.484
31020.0062 | 27.5919 | 32.3324 | 892.1125
31035.0062 | 27.5946 | 32.3243 | 891.9754
31050.0062 | 27.5933 | 32.3004 | 891.274
31065.0062 | 27.595 | 32.3305 | 892.161
31080.0062 | 27.5945 | 32.3964 | 893.9616
31095.0062 | 27.5978 | 32.4084 | 894.3995
31110.0062 | 27.5976 | 32.3411 | 892.5368
31125.0062 | 27.5978 | 32.3785 | 893.5749
31140.0062 | 27.6019 | 32.3107 | 891.8367
31155.0062 | 27.5998 | 32.4186 | 894.7476
31170.0062 | 27.6002 | 32.295 | 891.3496
31185.0062 | 27.6028 | 32.3565 | 893.1298
31200.0062 | 27.6017 | 32.4136 | 894.6694
31215.0062 | 27.6024 | 32.3678 | 893.4275
31230.0062 | 27.6046 | 32.43 | 895.2175
31245.0062 | 27.6036 | 32.4255 | 895.0593
31260.0062 | 27.6065 | 32.3722 | 893.6824
31275.0062 | 27.6071 | 32.3225 | 892.3298
31290.0062 | 27.6081 | 32.3733 | 893.7646
31305.0062 | 27.6092 | 32.4012 | 894.5696
31320.0062 | 27.6076 | 32.2918 | 891.4989
31335.0062 | 27.6072 | 32.3139 | 892.0939
31350.0062 | 27.6101 | 32.3281 | 892.5841
31365.0062 | 27.4625 | 27.0743 | 743.5299
31380.0062 | 27.6045 | 32.3536 | 893.1039
31395.0062 | 27.6101 | 32.378 | 893.9599
31410.0062 | 27.6119 | 32.3778 | 894.0124
31425.0062 | 27.6123 | 32.3666 | 893.7147
31440.0062 | 27.6142 | 32.4099 | 894.9745
31455.0062 | 27.6155 | 32.3648 | 893.7703
31470.0062 | 27.6153 | 32.2969 | 891.8862
31485.0062 | 27.617 | 32.3373 | 893.0591
31500.0062 | 27.617 | 32.3478 | 893.3516
31515.0062 | 27.6169 | 32.3829 | 894.3151
31530.0062 | 27.6192 | 32.3217 | 892.7006
31545.0062 | 27.6207 | 32.4165 | 895.3663
31560.0062 | 27.6208 | 32.228 | 890.1622
31575.0062 | 27.6219 | 32.406 | 895.1161
31590.0062 | 27.622 | 32.284 | 891.7494
31605.0062 | 27.624 | 32.3981 | 894.9667
31620.0062 | 27.624 | 32.2989 | 892.2267
31635.0062 | 27.6241 | 32.3393 | 893.3422
31650.0062 | 27.6258 | 32.268 | 891.4283
31665.0062 | 27.627 | 32.3253 | 893.0516
31680.0062 | 27.6292 | 32.404 | 895.296
31695.0062 | 27.6284 | 32.2864 | 892.0215
31710.0062 | 27.6301 | 32.3535 | 893.9289
31725.0062 | 27.6296 | 32.3931 | 895.0087
31740.0062 | 27.6319 | 32.379 | 894.6917
31755.0062 | 27.633 | 32.2579 | 891.3835
31770.0062 | 27.6326 | 32.3018 | 892.5831
31785.0062 | 27.6349 | 32.3308 | 893.4575
31800.0062 | 27.635 | 32.386 | 894.9873
31815.0062 | 27.6372 | 32.3778 | 894.832
31830.0062 | 27.6381 | 32.3188 | 893.2306
31845.0062 | 27.6401 | 32.3033 | 892.8694
31860.0062 | 27.6403 | 32.3126 | 893.1289
31875.0062 | 27.6386 | 32.3063 | 892.9036
31890.0062 | 27.6412 | 32.2894 | 892.5185
31905.0062 | 27.6428 | 32.215 | 890.5131
31920.0062 | 27.6428 | 32.3884 | 895.3073
31935.0062 | 27.6446 | 32.2723 | 892.1556
31950.0062 | 27.6447 | 32.2349 | 891.1259
31965.0062 | 27.48 | 29.0967 | 799.5769
31980.0062 | 27.6437 | 32.277 | 892.2577
31995.0062 | 27.646 | 32.2814 | 892.4509
32010.0062 | 27.6486 | 32.3569 | 894.6227
32025.0062 | 27.6492 | 32.2922 | 892.8539
32040.0062 | 27.6511 | 32.3316 | 894.0053
32055.0062 | 27.6515 | 32.3351 | 894.1141
32070.0062 | 27.6521 | 32.2911 | 892.9167
32085.0062 | 27.6533 | 32.2692 | 892.3492
32100.0062 | 27.6545 | 32.2227 | 891.1001
32115.0062 | 27.6544 | 32.2394 | 891.5603
32130.0062 | 27.6582 | 32.2546 | 892.1037
32145.0062 | 27.658 | 32.2823 | 892.865
32160.0062 | 27.6592 | 32.2382 | 891.6836
32175.0062 | 27.6594 | 32.2327 | 891.539
32190.0062 | 27.662 | 32.3548 | 894.9998
32205.0062 | 27.6611 | 32.3111 | 893.7595
32220.0062 | 27.6639 | 32.2841 | 893.1061
32235.0062 | 27.664 | 32.2233 | 891.427
32250.0062 | 27.6677 | 32.3463 | 894.9462
32265.0062 | 27.668 | 32.3114 | 893.9936
32280.0062 | 27.6688 | 32.2656 | 892.7503
32295.0062 | 27.6702 | 32.2571 | 892.558
32310.0062 | 27.6692 | 32.2809 | 893.1872
32325.0062 | 27.6709 | 32.2741 | 893.0536
32340.0062 | 27.6713 | 32.2162 | 891.466
32355.0062 | 27.6716 | 32.3395 | 894.8837
32370.0062 | 27.6768 | 32.2227 | 891.8209
32385.0062 | 27.6763 | 32.2671 | 893.0347
32400.0062 | 27.6761 | 32.3407 | 895.0635
32415.0062 | 27.6789 | 32.2673 | 893.1247
32430.0062 | 27.6796 | 32.3085 | 894.2864
32445.0062 | 27.6788 | 32.2506 | 892.6594
32460.0062 | 27.6821 | 32.2269 | 892.1097
32475.0062 | 27.6817 | 32.3287 | 894.913
32490.0062 | 27.6821 | 32.3168 | 894.5985
32505.0062 | 27.6852 | 32.2931 | 894.042
32520.0062 | 27.6843 | 32.2736 | 893.4739
32535.0062 | 27.688 | 32.2564 | 893.1157
32550.0062 | 27.6868 | 32.3081 | 894.5076
32565.0062 | 27.5464 | 28.8813 | 795.5756
32580.0062 | 27.5682 | 32.2223 | 888.311
32595.0062 | 27.6959 | 32.2357 | 892.7957
32610.0062 | 27.6956 | 32.2345 | 892.7529
32625.0062 | 27.6989 | 32.2843 | 894.24
32640.0062 | 27.6989 | 32.2274 | 892.6644
32655.0062 | 27.7017 | 32.2923 | 894.5498
32670.0062 | 27.7009 | 32.3133 | 895.1066
32685.0062 | 27.7033 | 32.2579 | 893.6497
32700.0062 | 27.7054 | 32.2318 | 892.9969
32715.0062 | 27.7039 | 32.2203 | 892.6292
32730.0062 | 27.7059 | 32.2678 | 894.0108
32745.0062 | 27.707 | 32.2196 | 892.7077
32760.0062 | 27.7055 | 32.1588 | 890.9746
32775.0062 | 27.7075 | 32.1817 | 891.6749
32790.0062 | 27.7092 | 32.1914 | 891.9961
32805.0062 | 27.7115 | 32.2093 | 892.5677
32820.0062 | 27.7103 | 32.2986 | 895.0023
32835.0062 | 27.7131 | 32.209 | 892.6107
32850.0063 | 27.7124 | 32.1955 | 892.2153
32865.0062 | 27.715 | 32.2311 | 893.2863
32880.0062 | 27.7139 | 32.2425 | 893.5663
32895.0062 | 27.714 | 32.2442 | 893.6171
32910.0062 | 27.7146 | 32.2039 | 892.5167
32925.0062 | 27.7163 | 32.1362 | 890.6963
32940.0062 | 27.7158 | 32.1934 | 892.2665
32955.0062 | 27.7161 | 32.1611 | 891.3793
32970.0062 | 27.7175 | 32.2125 | 892.8514
32985.0062 | 27.7169 | 32.2539 | 893.9771
33000.0062 | 27.7181 | 32.2876 | 894.9518
33015.0062 | 27.7172 | 32.2022 | 892.5563
33030.0062 | 27.72 | 32.2113 | 892.8961
33045.0062 | 27.7212 | 32.2075 | 892.8313
33060.0062 | 27.7199 | 32.2585 | 894.2023
33075.0062 | 27.7219 | 32.1895 | 892.3525
33090.0062 | 27.7224 | 32.2049 | 892.7977
33105.0062 | 27.7223 | 32.1904 | 892.3914
33120.0062 | 27.7228 | 32.2032 | 892.7646
33135.0062 | 27.7239 | 32.1302 | 890.7763
33150.0062 | 27.7235 | 32.2165 | 893.1566
33165.0062 | 27.5765 | 28.6216 | 789.2833
33180.0062 | 27.7195 | 32.1569 | 891.3709
33195.0062 | 27.7217 | 32.1461 | 891.1434
33210.0062 | 27.7223 | 32.144 | 891.1062
33225.0062 | 27.7246 | 32.232 | 893.6211
33240.0062 | 27.7258 | 32.2342 | 893.7181
33255.0062 | 27.7234 | 32.2844 | 895.0335
33270.0062 | 27.7273 | 32.2075 | 893.029
33285.0062 | 27.7272 | 32.2229 | 893.451
33300.0062 | 27.7281 | 32.1753 | 892.1613
33315.0062 | 27.7291 | 32.243 | 894.0713
33330.0062 | 27.7291 | 32.2685 | 894.7767
33345.0062 | 27.7272 | 32.1788 | 892.2296
33360.0062 | 27.7302 | 32.2348 | 893.8777
33375.0062 | 27.7283 | 32.1872 | 892.4949
33390.0062 | 27.7286 | 32.2502 | 894.2536
33405.0062 | 27.7314 | 32.1882 | 892.6237
33420.0062 | 27.733 | 32.2685 | 894.9009
33435.0062 | 27.7326 | 32.2842 | 895.3239
33450.0062 | 27.7311 | 32.1501 | 891.5581
33465.0062 | 27.7318 | 32.2155 | 893.3938
33480.0062 | 27.7328 | 32.2701 | 894.9409
33495.0062 | 27.7306 | 32.1288 | 890.9501
33510.0062 | 27.7302 | 32.1836 | 892.4587
33525.0062 | 27.7316 | 32.2536 | 894.4441
33540.0062 | 27.7317 | 32.0797 | 889.6236
33555.0062 | 27.7348 | 32.2804 | 895.2892
33570.0062 | 27.7322 | 32.1737 | 892.2468
33585.0062 | 27.7333 | 32.2038 | 893.1181
33600.0062 | 27.7333 | 32.1678 | 892.1208
33615.0062 | 27.7311 | 32.2227 | 893.5714
33630.0062 | 27.7352 | 32.2064 | 893.2526
33645.0062 | 27.734 | 32.1432 | 891.4603
33660.0062 | 27.733 | 32.1063 | 890.4031
33675.0062 | 27.7335 | 32.154 | 891.7445
33690.0062 | 27.7359 | 32.1702 | 892.2703
33705.0062 | 27.7344 | 32.2031 | 893.1329
33720.0062 | 27.7362 | 32.164 | 892.1064
33735.0062 | 27.7373 | 32.1113 | 890.6831
33750.0062 | 27.7356 | 32.143 | 891.5033
33765.0062 | 27.5579 | 29.5554 | 814.4851
33780.0062 | 27.7318 | 32.1297 | 891.0153
33795.0062 | 27.7329 | 32.1444 | 891.4562
33810.0062 | 27.7356 | 32.2514 | 894.5123
33825.0062 | 27.733 | 32.142 | 891.3952
33840.0062 | 27.7363 | 32.2222 | 893.7246
33855.0062 | 27.7382 | 32.2138 | 893.5522
33870.0062 | 27.7375 | 32.1656 | 892.1923
33885.0062 | 27.7395 | 32.1827 | 892.7335
33900.0062 | 27.739 | 32.2498 | 894.5782
33915.0062 | 27.7393 | 32.154 | 891.9296
33930.0062 | 27.7391 | 32.2555 | 894.7376
33945.0062 | 27.7396 | 32.2336 | 894.1463
33960.0062 | 27.7374 | 32.2256 | 893.8543
33975.0062 | 27.74 | 32.2415 | 894.3771
33990.0062 | 27.7407 | 32.1941 | 893.0876
34005.0062 | 27.7395 | 32.1841 | 892.7714
34020.0062 | 27.7404 | 32.2224 | 893.8635
34035.0062 | 27.7402 | 32.1999 | 893.2319
34050.0062 | 27.7421 | 32.2816 | 895.5595
34065.0062 | 27.7405 | 32.2301 | 894.0794
34080.0062 | 27.7394 | 32.1912 | 892.9657
34095.0062 | 27.7421 | 32.159 | 892.1574
34110.0062 | 27.743 | 32.2094 | 893.587
34125.0062 | 27.7415 | 32.1653 | 892.313
34140.0062 | 27.7421 | 32.2466 | 894.5867
34155.0062 | 27.7413 | 32.1068 | 890.684
34170.0062 | 27.7384 | 32.2411 | 894.3156
34185.0062 | 27.7428 | 32.2238 | 893.9805
34200.0062 | 27.7409 | 32.2114 | 893.5719
34215.0062 | 27.7401 | 32.1587 | 892.0854
34230.0062 | 27.7394 | 32.1505 | 891.838
34245.0062 | 27.7407 | 32.2582 | 894.8652
34260.0062 | 27.7415 | 32.219 | 893.8013
34275.0062 | 27.742 | 32.2537 | 894.7818
34290.0062 | 27.7401 | 32.0812 | 889.9382
34305.0062 | 27.7441 | 32.2086 | 893.5993
34320.0062 | 27.7419 | 32.1826 | 892.8064
34335.0062 | 27.7416 | 32.1757 | 892.6051
34350.0062 | 27.7415 | 32.2236 | 893.9335
34365.0062 | 27.588 | 28.1902 | 777.71
34380.0062 | 27.7363 | 32.2799 | 895.3228
34395.0062 | 27.7381 | 32.1781 | 892.5595
34410.0062 | 27.7399 | 32.1882 | 892.8981
34425.0062 | 27.7397 | 32.1412 | 891.5852
34440.0062 | 27.7424 | 32.2367 | 894.3216
34455.0062 | 27.7422 | 32.1841 | 892.8568
34470.0062 | 27.7429 | 32.1567 | 892.1184
34485.0062 | 27.7418 | 32.2849 | 895.6399
34500.0062 | 27.7412 | 32.145 | 891.7416
34515.0062 | 27.7428 | 32.1266 | 891.2814
34530.0062 | 27.742 | 32.2415 | 894.4423
34545.0062 | 27.7408 | 32.2208 | 893.8293
34560.0062 | 27.7406 | 32.2084 | 893.4806
34575.0062 | 27.7417 | 32.2702 | 895.228
34590.0062 | 27.7401 | 32.1082 | 890.6845
34605.0062 | 27.7425 | 32.2452 | 894.5618
34620.0062 | 27.7435 | 32.2268 | 894.0855
34635.0062 | 27.7406 | 32.1774 | 892.6187
34650.0062 | 27.7434 | 32.2191 | 893.8701
34665.0062 | 27.7416 | 32.2093 | 893.5383
34680.0062 | 27.7417 | 32.2082 | 893.512
34695.0062 | 27.7427 | 32.2281 | 894.0972
34710.0062 | 27.7439 | 32.1824 | 892.8666
34725.0062 | 27.7418 | 32.1125 | 890.8585
34740.0062 | 27.7431 | 32.1953 | 893.1975
34755.0062 | 27.7426 | 32.1327 | 891.4444
34770.0062 | 27.742 | 32.2006 | 893.3098
34785.0062 | 27.743 | 32.1746 | 892.6196
34800.0062 | 27.7423 | 32.2293 | 894.1129
34815.0062 | 27.7435 | 32.1089 | 890.8121
34830.0062 | 27.7436 | 32.2497 | 894.7239
34845.0062 | 27.7424 | 32.2144 | 893.7048
34860.0062 | 27.7425 | 32.2228 | 893.9407
34875.0062 | 27.7422 | 32.2086 | 893.5384
34890.0062 | 27.7417 | 32.1949 | 893.1399
34905.0062 | 27.7445 | 32.2172 | 893.85
34920.0062 | 27.7451 | 32.231 | 894.2512
34935.0062 | 27.7434 | 32.2244 | 894.0151
34950.0062 | 27.7433 | 32.2379 | 894.3872
34965.0062 | 27.6409 | 32.2383 | 891.0967
34980.0062 | 27.7405 | 32.2026 | 893.3168
34995.0062 | 27.7422 | 32.1924 | 893.0878
35010.0062 | 27.7445 | 32.2347 | 894.3344
35025.0062 | 27.7434 | 32.1162 | 891.0129
35040.0062 | 27.7452 | 32.2297 | 894.2179
35055.0062 | 27.7461 | 32.2048 | 893.558
35070.0062 | 27.742 | 32.2513 | 894.7141
35085.0062 | 27.7444 | 32.2532 | 894.8451
35100.0062 | 27.7456 | 32.2516 | 894.839
35115.0062 | 27.7456 | 32.1596 | 892.2861
35130.0062 | 27.7422 | 32.1934 | 893.1184
35145.0062 | 27.7452 | 32.1832 | 892.9294
35160.0062 | 27.7457 | 32.2076 | 893.6235
35175.0062 | 27.7444 | 32.2038 | 893.4748
35190.0062 | 27.7448 | 32.1689 | 892.518
35205.0062 | 27.7464 | 32.2093 | 893.6898
35220.0062 | 27.7429 | 32.2711 | 895.293
35235.0062 | 27.7453 | 32.1576 | 892.223
35250.0062 | 27.7453 | 32.1124 | 890.9679
35265.0062 | 27.7463 | 32.2348 | 894.3976
35280.0062 | 27.7439 | 32.1883 | 893.0303
35295.0062 | 27.7454 | 32.1719 | 892.6225
35310.0062 | 27.7452 | 32.2318 | 894.2799
35325.0062 | 27.7463 | 32.1967 | 893.3388
35340.0062 | 27.7453 | 32.2457 | 894.6647
35355.0062 | 27.7467 | 32.2454 | 894.7054
35370.0062 | 27.7465 | 32.1751 | 892.7477
35385.0062 | 27.7424 | 32.2172 | 893.7833
35400.0062 | 27.7457 | 32.2373 | 894.447
35415.0062 | 27.7442 | 32.2018 | 893.4143
35430.0062 | 27.7448 | 32.1705 | 892.5665
35445.0062 | 27.7455 | 32.1589 | 892.2664
35460.0062 | 27.7469 | 32.2386 | 894.5203
35475.0062 | 27.7466 | 32.2392 | 894.5271
35490.0062 | 27.7454 | 32.2185 | 893.9154
35505.0062 | 27.7464 | 32.2236 | 894.0867
35520.0062 | 27.7473 | 32.1849 | 893.0419
35535.0062 | 27.7474 | 32.2259 | 894.1845
35550.0062 | 27.7473 | 32.1509 | 892.0999
35565.0062 | 27.6504 | 27.1568 | 750.896
35580.0062 | 27.6505 | 32.2619 | 892.0587
35595.0062 | 27.7457 | 32.1423 | 891.8108
35610.0062 | 27.7467 | 32.2421 | 894.6133
35625.0062 | 27.7466 | 32.2577 | 895.0434
35640.0062 | 27.7486 | 32.1314 | 891.6002
35655.0062 | 27.7477 | 32.2393 | 894.5638
35670.0062 | 27.7492 | 32.1697 | 892.6843
35685.0062 | 27.7497 | 32.1999 | 893.5391
35700.0062 | 27.7503 | 32.2399 | 894.6675
35715.0062 | 27.7498 | 32.1979 | 893.485
35730.0062 | 27.7488 | 32.248 | 894.8406
35745.0062 | 27.7509 | 32.1011 | 890.8335
35760.0062 | 27.7501 | 32.1269 | 891.5222
35775.0062 | 27.7496 | 32.2246 | 894.2197
35790.0062 | 27.7494 | 32.2534 | 895.01
35805.0062 | 27.7507 | 32.2211 | 894.1582
35820.0062 | 27.7488 | 32.1558 | 892.2853
35835.0062 | 27.7514 | 32.2146 | 893.9995
35850.0062 | 27.7489 | 32.2116 | 893.8363
35865.0062 | 27.7495 | 32.2377 | 894.5814
35880.0062 | 27.7498 | 32.228 | 894.3198
35895.0062 | 27.7497 | 32.1338 | 891.7038
35910.0062 | 27.7502 | 32.1796 | 892.9899
35925.0062 | 27.751 | 32.2144 | 893.9826
35940.0062 | 27.752 | 32.1768 | 892.9697
35955.0062 | 27.7507 | 32.1731 | 892.8255
35970.0062 | 27.7504 | 32.1999 | 893.5594
35985.0062 | 27.7514 | 32.2691 | 895.5141
36000.0062 | 27.7503 | 32.2338 | 894.4969
36015.0062 | 27.7514 | 32.1564 | 892.3833
36030.0062 | 27.7519 | 32.1899 | 893.3308
36045.0062 | 27.7496 | 32.1231 | 891.4015
36060.0062 | 27.7512 | 32.2607 | 895.2754
36075.0062 | 27.7531 | 32.2385 | 894.7179
36090.0062 | 27.7518 | 32.152 | 892.2739
36105.0062 | 27.7516 | 32.2118 | 893.9272
36120.0062 | 27.7516 | 32.1607 | 892.5119
36135.0062 | 27.7514 | 32.2039 | 893.7046
36150.0062 | 27.7523 | 31.7725 | 881.7595
36165.0062 | 27.6075 | 26.8151 | 740.2972
36180.0062 | 27.747 | 32.2012 | 893.4877
36195.0062 | 27.7484 | 32.1426 | 891.9071
36210.0062 | 27.7514 | 32.1936 | 893.4184
36225.0062 | 27.7501 | 32.1781 | 892.9438
36240.0062 | 27.7511 | 32.2309 | 894.4437
36255.0062 | 27.7511 | 32.2328 | 894.4943
36270.0062 | 27.7514 | 32.1766 | 892.9465
36285.0062 | 27.7505 | 32.1191 | 891.3234
36300.0062 | 27.7511 | 32.1522 | 892.2599
36315.0062 | 27.7529 | 32.1906 | 893.3832
36330.0062 | 27.7518 | 32.1822 | 893.1154
36345.0062 | 27.7539 | 32.1144 | 891.3014
36360.0062 | 27.755 | 32.1739 | 892.9874
36375.0062 | 27.7545 | 32.2578 | 895.2979
36390.0062 | 27.753 | 32.2545 | 895.159
36405.0062 | 27.7528 | 32.2217 | 894.242
36420.0062 | 27.7542 | 32.1692 | 892.8288
36435.0062 | 27.7562 | 32.1815 | 893.2381
36450.0062 | 27.7543 | 32.1732 | 892.9447
36465.0062 | 27.7558 | 32.1992 | 893.7146
36480.0062 | 27.7542 | 32.1 | 890.9088
36495.0062 | 27.7555 | 32.2561 | 895.2857
36510.0062 | 27.752 | 32.1917 | 893.3863
36525.0062 | 27.7537 | 32.1807 | 893.1327
36540.0062 | 27.7558 | 32.211 | 894.0421
36555.0062 | 27.7544 | 32.1995 | 893.6776
36570.0062 | 27.7558 | 32.2168 | 894.2047
36585.0062 | 27.754 | 32.2131 | 894.0424
36600.0062 | 27.7541 | 32.1631 | 892.6562
36615.0062 | 27.7546 | 32.2349 | 894.666
36630.0062 | 27.7552 | 32.18 | 893.1633
36645.0062 | 27.7544 | 32.2145 | 894.0947
36660.0062 | 27.7556 | 32.1734 | 892.9921
36675.0062 | 27.7538 | 32.1802 | 893.1249
36690.0062 | 27.7552 | 32.1897 | 893.4294
36705.0062 | 27.7551 | 32.211 | 894.02
36720.0062 | 27.7575 | 32.1477 | 892.3407
36735.0062 | 27.761 | 32.1875 | 893.5556
36750.0062 | 27.7608 | 32.1317 | 892.003
36765.0062 | 27.6749 | 26.2621 | 726.7984
36780.0062 | 27.7522 | 32.1502 | 892.24
36795.0062 | 27.758 | 32.1655 | 892.8489
36810.0062 | 27.7582 | 32.1439 | 892.2555
36825.0062 | 27.7585 | 32.2619 | 895.5405
36840.0062 | 27.7603 | 32.1561 | 892.663
36855.0062 | 27.7637 | 32.0871 | 890.8569
36870.0062 | 27.7658 | 32.1511 | 892.7027
36885.0062 | 27.7661 | 32.2124 | 894.4134
36900.0062 | 27.7663 | 32.144 | 892.5193
36915.0062 | 27.764 | 32.2451 | 895.2541
36930.0062 | 27.7662 | 32.1955 | 893.9462
36945.0062 | 27.765 | 32.1675 | 893.1305
36960.0062 | 27.767 | 32.1437 | 892.5353
36975.0062 | 27.7657 | 32.2424 | 895.2313
36990.0062 | 27.7674 | 32.1016 | 891.378
37005.0062 | 27.7653 | 32.1261 | 891.991
37020.0062 | 27.7684 | 32.1768 | 893.4964
37035.0062 | 27.766 | 32.1409 | 892.4267
37050.0062 | 27.7662 | 32.123 | 891.9346
37065.0062 | 27.767 | 32.16 | 892.9864
37080.0062 | 27.767 | 32.1512 | 892.7421
37095.0062 | 27.7675 | 32.1099 | 891.6101
37110.0062 | 27.7688 | 32.1506 | 892.7812
37125.0062 | 27.7671 | 32.1568 | 892.9006
37140.0062 | 27.7673 | 32.1481 | 892.6639
37155.0062 | 27.7691 | 32.1702 | 893.3369
37170.0062 | 27.7683 | 32.2403 | 895.2582
37185.0062 | 27.7679 | 32.1651 | 893.1572
37200.0062 | 27.7688 | 32.1424 | 892.5559
37215.0062 | 27.7679 | 32.1421 | 892.5175
37230.0062 | 27.7668 | 32.151 | 892.7296
37245.0062 | 27.7672 | 32.1485 | 892.6761
37260.0062 | 27.7687 | 32.1353 | 892.3563
37275.0062 | 27.7664 | 32.1383 | 892.3658
37290.0062 | 27.7676 | 32.1675 | 893.2158
37305.0062 | 27.7688 | 32.1183 | 891.886
37320.0062 | 27.7681 | 32.1759 | 893.4635
37335.0062 | 27.7694 | 32.1158 | 891.839
37350.0062 | 27.7699 | 29.0071 | 805.5249
37365.0062 | 27.6882 | 27.576 | 763.53
37380.0062 | 27.763 | 32.2218 | 894.572
37395.0062 | 27.7664 | 32.2082 | 894.3058
37410.0062 | 27.7675 | 32.1115 | 891.656
37425.0062 | 27.767 | 32.1122 | 891.6603
37440.0062 | 27.7708 | 32.1178 | 891.9354
37455.0062 | 27.7683 | 32.1351 | 892.3391
37470.0062 | 27.7683 | 32.041 | 889.7256
37485.0062 | 27.7703 | 32.0814 | 890.9109
37500.0062 | 27.7686 | 32.1629 | 893.1209
37515.0062 | 27.7681 | 32.1833 | 893.6679
37530.0062 | 27.7696 | 32.184 | 893.7382
37545.0062 | 27.7704 | 32.1402 | 892.546
37560.0062 | 27.7729 | 32.1364 | 892.5221
37575.0062 | 27.7716 | 32.1506 | 892.8715
37590.0062 | 27.7702 | 32.1513 | 892.8471
37605.0062 | 27.7706 | 32.1969 | 894.1274
37620.0062 | 27.7727 | 32.1634 | 893.2641
37635.0062 | 27.7707 | 32.1749 | 893.5188
37650.0062 | 27.7723 | 32.1399 | 892.5983
37665.0062 | 27.7708 | 32.1455 | 892.7064
37680.0062 | 27.7716 | 32.1498 | 892.8524
37695.0062 | 27.7715 | 32.1653 | 893.2787
37710.0062 | 27.7724 | 32.0948 | 891.3496
37725.0062 | 27.7718 | 32.1289 | 892.2775
37740.0062 | 27.7724 | 32.1668 | 893.3498
37755.0062 | 27.7735 | 32.1417 | 892.6855
37770.0062 | 27.7722 | 32.166 | 893.3216
37785.0062 | 27.7725 | 32.1217 | 892.099
37800.0062 | 27.7731 | 32.1771 | 893.6591
37815.0062 | 27.773 | 32.1096 | 891.7799
37830.0062 | 27.7725 | 32.1806 | 893.7354
37845.0062 | 27.7744 | 32.1527 | 893.02
37860.0062 | 27.7722 | 32.1798 | 893.7033
37875.0062 | 27.7738 | 32.1841 | 893.8759
37890.0062 | 27.7715 | 32.1369 | 892.4898
37905.0062 | 27.7731 | 32.1056 | 891.6729
37920.0062 | 27.7743 | 32.1387 | 892.6303
37935.0062 | 27.7745 | 32.167 | 893.4225
37950.0062 | 27.7729 | 26.5749 | 738.0604
37965.0062 | 27.6886 | 26.5696 | 735.6751
37980.0062 | 27.7678 | 32.14 | 892.4577
37995.0062 | 27.7708 | 32.1797 | 893.6567
38010.0062 | 27.7728 | 32.1386 | 892.5811
38025.0062 | 27.7723 | 32.1801 | 893.7147
38040.0062 | 27.7744 | 32.1198 | 892.1096
38055.0062 | 27.7745 | 32.1751 | 893.6447
38070.0062 | 27.7722 | 32.1687 | 893.3961
38085.0062 | 27.7745 | 32.1334 | 892.4876
38100.0062 | 27.7742 | 32.2198 | 894.8777
38115.0062 | 27.7757 | 32.1704 | 893.5536
38130.0062 | 27.7736 | 32.21 | 894.5865
38145.0062 | 27.7765 | 32.1036 | 891.7278
38160.0062 | 27.7739 | 32.1096 | 891.8079
38175.0062 | 27.7743 | 32.1573 | 893.1485
38190.0062 | 27.7749 | 32.1024 | 891.6418
38205.0062 | 27.776 | 32.056 | 890.388
38220.0062 | 27.7771 | 32.2149 | 894.8367
38235.0062 | 27.7746 | 32.2198 | 894.892
38250.0062 | 27.7756 | 32.1109 | 891.9014
38265.0062 | 27.7765 | 32.1596 | 893.2798
38280.0062 | 27.7743 | 32.1299 | 892.3837
38295.0062 | 27.7756 | 32.1044 | 891.7188
38310.0062 | 27.7791 | 32.1204 | 892.2745
38325.0062 | 27.7753 | 32.1805 | 893.8237
38340.0062 | 27.7774 | 32.0908 | 891.3991
38355.0062 | 27.7758 | 32.0816 | 891.0933
38370.0062 | 27.777 | 32.192 | 894.1987
38385.0062 | 27.7758 | 32.1274 | 892.3665
38400.0062 | 27.7765 | 31.9682 | 887.9648
38415.0062 | 27.7777 | 31.9492 | 887.4756
38430.0062 | 27.7775 | 32.1147 | 892.0667
38445.0062 | 27.7795 | 32.0967 | 891.6295
38460.0062 | 27.7782 | 32.2075 | 894.6649
38475.0062 | 27.7791 | 32.1734 | 893.7484
38490.0062 | 27.7799 | 32.1166 | 892.1975
38505.0062 | 27.7777 | 32.1678 | 893.5491
38520.0062 | 27.7782 | 32.2412 | 895.6017
38535.0062 | 27.7806 | 32.112 | 892.0896
38550.0062 | 27.7811 | 26.8321 | 745.4257
38565.0062 | 27.7732 | 32.0826 | 891.0368
38580.0062 | 27.7744 | 32.0845 | 891.1271
38595.0062 | 27.7763 | 32.0824 | 891.1294
38610.0062 | 27.7793 | 32.1555 | 893.2593
38625.0062 | 27.7793 | 32.1518 | 893.1523
38640.0062 | 27.7786 | 32.188 | 894.1376
38655.0062 | 27.7794 | 32.1648 | 893.5183
38670.0062 | 27.7786 | 32.1033 | 891.7855
38685.0062 | 27.7797 | 32.1643 | 893.5155
38700.0062 | 27.7799 | 32.125 | 892.4301
38715.0062 | 27.7796 | 32.1247 | 892.4115
38730.0062 | 27.7815 | 32.0798 | 891.2264
38745.0062 | 27.7796 | 32.1473 | 893.0386
38760.0062 | 27.7809 | 32.1749 | 893.848
38775.0062 | 27.7835 | 32.0564 | 890.6366
38790.0062 | 27.7824 | 32.1559 | 893.3666
38805.0062 | 27.7801 | 32.1371 | 892.7705
38820.0062 | 27.7815 | 32.1761 | 893.9009
38835.0062 | 27.7821 | 32.1343 | 892.7585
38850.0062 | 27.7819 | 32.1502 | 893.1931
38865.0062 | 27.7832 | 32.0834 | 891.3786
38880.0062 | 27.7807 | 32.1031 | 891.8474
38895.0062 | 27.7827 | 32.1396 | 892.9243
38910.0062 | 27.7815 | 32.1129 | 892.1452
38925.0062 | 27.7835 | 32.1147 | 892.2601
38940.0062 | 27.782 | 32.1642 | 893.5867
38955.0062 | 27.7835 | 32.1132 | 892.2167
38970.0062 | 27.784 | 32.0769 | 891.2254
38985.0062 | 27.7824 | 32.1589 | 893.4534
39000.0062 | 27.7818 | 32.1468 | 893.0983
39015.0062 | 27.7833 | 32.1435 | 893.0498
39030.0062 | 27.7835 | 32.1751 | 893.9389
39045.0062 | 27.7822 | 32.1544 | 893.3189
39060.0062 | 27.7843 | 32.1903 | 894.3857
39075.0062 | 27.783 | 32.1549 | 893.3592
39090.0062 | 27.7834 | 32.1179 | 892.343
39105.0062 | 27.782 | 32.0985 | 891.7611
39120.0062 | 27.783 | 32.1303 | 892.6755
39135.0062 | 27.7844 | 32.1786 | 894.0625
39150.0062 | 27.7843 | 30.9016 | 858.5794
39165.0062 | 27.6386 | 28.1966 | 779.3139
39180.0062 | 27.7801 | 32.1226 | 892.3683
39195.0062 | 27.782 | 32.1931 | 894.3902
39210.0062 | 27.7827 | 32.1013 | 891.8605
39225.0062 | 27.7843 | 32.1342 | 892.8261
39240.0062 | 27.785 | 32.1748 | 893.977
39255.0062 | 27.7831 | 32.0705 | 891.0164
39270.0062 | 27.7846 | 32.1311 | 892.7515
39285.0062 | 27.7838 | 32.1077 | 892.0742
39300.0062 | 27.7843 | 32.1647 | 893.6733
39315.0062 | 27.7847 | 32.1364 | 892.9015
39330.0062 | 27.7857 | 32.1545 | 893.4339
39345.0062 | 27.7856 | 32.166 | 893.753
39360.0062 | 27.7867 | 32.1033 | 892.0457
39375.0062 | 27.7864 | 32.1109 | 892.247
39390.0062 | 27.7827 | 32.109 | 892.0733
39405.0062 | 27.7859 | 32.1584 | 893.5493
39420.0062 | 27.787 | 32.1516 | 893.3963
39435.0062 | 27.7868 | 32.1368 | 892.9801
39450.0062 | 27.7884 | 32.1462 | 893.2924
39465.0062 | 27.7871 | 32.2035 | 894.8433
39480.0062 | 27.7882 | 32.1672 | 893.8678
39495.0062 | 27.7881 | 32.0867 | 891.6278
39510.0062 | 27.7887 | 32.1377 | 893.0647
39525.0062 | 27.7894 | 32.1755 | 894.1375
39540.0063 | 27.7889 | 32.1706 | 893.9881
39555.0062 | 27.7875 | 32.1221 | 892.5939
39570.0062 | 27.7905 | 32.1134 | 892.4475
39585.0062 | 27.7893 | 32.0943 | 891.8776
39600.0062 | 27.7896 | 32.2009 | 894.8512
39615.0062 | 27.7907 | 32.1379 | 893.1346
39630.0062 | 27.7893 | 32.1775 | 894.1897
39645.0062 | 27.7905 | 32.118 | 892.5761
39660.0062 | 27.7875 | 32.1128 | 892.3343
39675.0062 | 27.7916 | 32.1211 | 892.6974
39690.0062 | 27.7911 | 32.1026 | 892.166
39705.0062 | 27.7897 | 32.1732 | 894.085
39720.0062 | 27.7892 | 32.1808 | 894.2805
39735.0062 | 27.7903 | 32.1543 | 893.5769
39750.0062 | 27.7867 | 25.5367 | 709.5811
39765.0062 | 27.6454 | 28.3585 | 783.9804
39780.0062 | 27.7841 | 32.1627 | 893.611
39795.0062 | 27.7877 | 32.0661 | 891.043
39810.0062 | 27.789 | 32.2327 | 895.7119
39825.0062 | 27.7869 | 32.1284 | 892.7504
39840.0062 | 27.789 | 32.1204 | 892.5946
39855.0062 | 27.7888 | 32.1768 | 894.1539
39870.0062 | 27.789 | 32.1706 | 893.9881
39885.0062 | 27.7902 | 32.1996 | 894.8309
39900.0062 | 27.7915 | 32.1191 | 892.6384
39915.0062 | 27.7931 | 32.0972 | 892.0797
39930.0062 | 27.7916 | 32.0869 | 891.7491
39945.0062 | 27.7923 | 32.088 | 891.7979
39960.0062 | 27.7914 | 32.1123 | 892.4454
39975.0062 | 27.7917 | 32.1801 | 894.3397
39990.0062 | 27.7929 | 32.1317 | 893.0324
40005.0062 | 27.7925 | 32.1256 | 892.8508
40020.0062 | 27.7934 | 32.076 | 891.5018
40035.0062 | 27.7909 | 32.0787 | 891.4952
40050.0062 | 27.7929 | 32.1047 | 892.2818
40065.0062 | 27.792 | 32.1262 | 892.8513
40080.0062 | 27.7918 | 32.1095 | 892.3779
40095.0062 | 27.7936 | 32.1324 | 893.0754
40110.0062 | 27.7932 | 32.0906 | 891.9002
40125.0062 | 27.7916 | 32.0859 | 891.7167
40140.0062 | 27.7904 | 32.1931 | 894.6586
40155.0062 | 27.7935 | 32.0693 | 891.3189
40170.0062 | 27.7959 | 32.1246 | 892.9315
40185.0062 | 27.795 | 32.0365 | 890.4552
40200.0062 | 27.7941 | 32.0962 | 892.087
40215.0062 | 27.7955 | 32.1904 | 894.7494
40230.0062 | 27.7932 | 32.114 | 892.5481
40245.0062 | 27.7924 | 32.1535 | 893.6235
40260.0062 | 27.796 | 32.1559 | 893.8051
40275.0062 | 27.7935 | 32.1138 | 892.5547
40290.0062 | 27.7969 | 32.0966 | 892.1865
40305.0062 | 27.7971 | 32.1093 | 892.5459
40320.0062 | 27.7934 | 32.1441 | 893.3941
40335.0062 | 27.7959 | 32.1864 | 894.6486
40350.0062 | 27.7853 | 25.9824 | 721.929
40365.0062 | 27.7903 | 32.0633 | 891.0513
40380.0062 | 27.7936 | 32.1279 | 892.9503
40395.0062 | 27.7936 | 32.1292 | 892.9862
40410.0062 | 27.795 | 32.0839 | 891.7716
40425.0062 | 27.7954 | 32.0779 | 891.6178
40440.0062 | 27.7963 | 32.1378 | 893.3115
40455.0062 | 27.7982 | 32.1647 | 894.1219
40470.0062 | 27.7959 | 32.1862 | 894.6425
40485.0062 | 27.7957 | 32.0506 | 890.8684
40500.0062 | 27.7995 | 32.1283 | 893.1492
40515.0062 | 27.7976 | 32.0916 | 892.0719
40530.0062 | 27.798 | 32.1374 | 893.3539
40545.0062 | 27.798 | 32.0611 | 891.2343
40560.0062 | 27.7994 | 32.1013 | 892.3951
40575.0062 | 27.7983 | 32.1807 | 894.5676
40590.0062 | 27.7998 | 32.1363 | 893.381
40605.0062 | 27.7978 | 32.1308 | 893.1662
40620.0062 | 27.7971 | 32.1563 | 893.852
40635.0062 | 27.7995 | 32.1176 | 892.8514
40650.0062 | 27.7997 | 32.1184 | 892.8802
40665.0062 | 27.7988 | 32.1402 | 893.4582
40680.0062 | 27.7984 | 32.1 | 892.3286
40695.0062 | 27.8005 | 32.1232 | 893.0424
40710.0062 | 27.7994 | 32.1136 | 892.7383
40725.0062 | 27.7989 | 32.1509 | 893.7608
40740.0062 | 27.7994 | 32.0845 | 891.9278
40755.0062 | 27.8009 | 32.1385 | 893.4803
40770.0062 | 27.7986 | 32.1628 | 894.0802
40785.0062 | 27.8008 | 32.0708 | 891.5932
40800.0062 | 27.8007 | 32.2051 | 895.3247
40815.0062 | 27.7997 | 32.1004 | 892.3833
40830.0062 | 27.7995 | 32.1116 | 892.6869
40845.0062 | 27.8002 | 32.1184 | 892.8999
40860.0062 | 27.7991 | 32.1222 | 892.9696
40875.0062 | 27.8028 | 32.1 | 892.4701
40890.0062 | 27.8028 | 32.1488 | 893.825
40905.0062 | 27.8024 | 32.0663 | 891.5178
40920.0062 | 27.8029 | 32.1492 | 893.843
40935.0062 | 27.8017 | 32.1123 | 892.7789
40950.0062 | 27.7993 | 28.8243 | 801.2943
40965.0062 | 27.635 | 32.1854 | 889.4426
40980.0062 | 27.7981 | 32.1508 | 893.7306
40995.0062 | 27.7999 | 32.0814 | 891.8624
41010.0062 | 27.7997 | 32.1112 | 892.6807
41025.0062 | 27.8015 | 32.1247 | 893.1144
41040.0062 | 27.8017 | 32.1201 | 892.9915
41055.0062 | 27.8013 | 32.1916 | 894.9685
41070.0062 | 27.8031 | 32.0057 | 889.8562
41085.0062 | 27.8032 | 32.1059 | 892.6452
41100.0062 | 27.8045 | 32.1339 | 893.4661
41115.0062 | 27.8027 | 31.9704 | 888.8622
41130.0062 | 27.8053 | 32.131 | 893.4127
41145.0062 | 27.8036 | 32.1745 | 894.5693
41160.0062 | 27.8035 | 32.0294 | 890.5288
41175.0062 | 27.8061 | 32.081 | 892.0496
41190.0062 | 27.8036 | 32.0695 | 891.6488
41205.0062 | 27.8022 | 32.0673 | 891.5414
41220.0062 | 27.8062 | 32.1927 | 895.1549
41235.0062 | 27.8067 | 32.1397 | 893.6995
41250.0062 | 27.8048 | 32.1836 | 894.8587
41265.0062 | 27.8052 | 32.1165 | 893.0053
41280.0062 | 27.8065 | 32.1156 | 893.0206
41295.0062 | 27.8055 | 32.0625 | 891.5114
41310.0062 | 27.8072 | 32.1563 | 894.1762
41325.0062 | 27.8073 | 32.1429 | 893.8048
41340.0062 | 27.8066 | 32.1357 | 893.5821
41355.0062 | 27.8085 | 32.1403 | 893.7749
41370.0062 | 27.8084 | 32.158 | 894.2611
41385.0062 | 27.8089 | 32.1289 | 893.4677
41400.0062 | 27.8078 | 32.1226 | 893.2607
41415.0062 | 27.8091 | 32.112 | 893.005
41430.0062 | 27.8081 | 32.1151 | 893.0613
41445.0062 | 27.8062 | 32.1192 | 893.1123
41460.0062 | 27.8086 | 32.086 | 892.2676
41475.0062 | 27.8085 | 32.1972 | 895.3558
41490.0062 | 27.8075 | 32.0902 | 892.3463
41505.0062 | 27.8089 | 32.1755 | 894.7643
41520.0062 | 27.8085 | 32.1483 | 893.9951
41535.0062 | 27.8092 | 32.1255 | 893.3833
41550.0062 | 27.8008 | 28.0529 | 779.8935
41565.0062 | 27.6405 | 29.4457 | 813.8917
41580.0062 | 27.8015 | 32.1127 | 892.7807
41595.0062 | 27.8049 | 32.2092 | 895.5724
41610.0062 | 27.806 | 32.1335 | 893.5018
41625.0062 | 27.8099 | 32.1675 | 894.5755
41640.0062 | 27.8086 | 32.1299 | 893.4886
41655.0062 | 27.8102 | 32.142 | 893.8769
41670.0062 | 27.81 | 32.0824 | 892.2128
41685.0062 | 27.8099 | 32.1685 | 894.6024
41700.0062 | 27.8112 | 32.1484 | 894.0863
41715.0062 | 27.8095 | 32.149 | 894.046
41730.0062 | 27.811 | 32.1679 | 894.6239
41745.0062 | 27.811 | 32.0863 | 892.3537
41760.0062 | 27.8117 | 32.093 | 892.5625
41775.0062 | 27.8123 | 32.0965 | 892.677
41790.0062 | 27.81 | 32.1707 | 894.6694
41805.0062 | 27.8133 | 32.0958 | 892.6915
41820.0062 | 27.8126 | 32.0194 | 890.542
41835.0062 | 27.8123 | 32.2136 | 895.9355
41850.0062 | 27.8124 | 32.1506 | 894.1858
41865.0062 | 27.8122 | 32.1695 | 894.7034
41880.0062 | 27.8133 | 32.1766 | 894.9366
41895.0062 | 27.813 | 32.1162 | 893.2468
41910.0062 | 27.8149 | 32.0918 | 892.6296
41925.0062 | 27.8127 | 32.1643 | 894.5757
41940.0062 | 27.8141 | 32.1221 | 893.4483
41955.0062 | 27.8141 | 32.1989 | 895.5842
41970.0062 | 27.8152 | 32.1634 | 894.6312
41985.0062 | 27.8144 | 32.152 | 894.2899
42000.0062 | 27.8149 | 32.1896 | 895.3506
42015.0062 | 27.8168 | 32.1156 | 893.3556
42030.0062 | 27.8135 | 32.1538 | 894.3108
42045.0062 | 27.8159 | 32.1491 | 894.2559
42060.0062 | 27.8145 | 32.105 | 892.9854
42075.0062 | 27.8144 | 32.1191 | 893.3733
42090.0062 | 27.8163 | 32.0898 | 892.62
42105.0062 | 27.8163 | 32.0765 | 892.249
42120.0062 | 27.8141 | 32.1795 | 895.0459
42135.0062 | 27.8161 | 32.1333 | 893.8242
42150.0062 | 27.8025 | 27.3511 | 760.429
42165.0062 | 27.7047 | 32.1708 | 891.2806
42180.0062 | 27.8111 | 32.141 | 893.8755
42195.0062 | 27.8138 | 32.0863 | 892.4411
42210.0062 | 27.8158 | 32.1854 | 895.2635
42225.0062 | 27.8154 | 32.1748 | 894.9571
42240.0062 | 27.8153 | 32.1737 | 894.9213
42255.0062 | 27.8173 | 32.1255 | 893.6458
42270.0062 | 27.8165 | 32.0881 | 892.5785
42285.0062 | 27.8173 | 32.0795 | 892.3645
42300.0062 | 27.819 | 32.1446 | 894.2307
42315.0062 | 27.8177 | 32.1011 | 892.9816
42330.0062 | 27.8169 | 32.1587 | 894.5535
42345.0062 | 27.8175 | 32.1467 | 894.239
42360.0062 | 27.8179 | 32.1016 | 892.9977
42375.0062 | 27.8197 | 32.1121 | 893.3473
42390.0062 | 27.8199 | 32.0698 | 892.1787
42405.0062 | 27.8181 | 32.1031 | 893.0467
42420.0062 | 27.8209 | 32.0997 | 893.0414
42435.0062 | 27.8182 | 32.0712 | 892.1617
42450.0062 | 27.8211 | 32.1838 | 895.3884
42465.0062 | 27.8195 | 32.127 | 893.7594
42480.0062 | 27.8208 | 32.0289 | 891.0692
42495.0062 | 27.8205 | 32.1586 | 894.6691
42510.0062 | 27.8213 | 32.0712 | 892.2627
42525.0062 | 27.8202 | 32.0858 | 892.6317
42540.0062 | 27.8203 | 32.0957 | 892.9104
42555.0062 | 27.8219 | 32.1559 | 894.6396
42570.0062 | 27.8204 | 32.0516 | 891.6874
42585.0062 | 27.8217 | 32.06 | 891.9654
42600.0062 | 27.8211 | 32.1347 | 894.0225
42615.0062 | 27.8204 | 32.0319 | 891.1379
42630.0062 | 27.8221 | 32.1661 | 894.9286
42645.0062 | 27.8212 | 32.1387 | 894.139
42660.0062 | 27.821 | 32.1763 | 895.1754
42675.0062 | 27.821 | 32.1203 | 893.6183
42690.0062 | 27.8245 | 32.1373 | 894.2046
42705.0062 | 27.8232 | 32.0652 | 892.1585
42720.0062 | 27.8227 | 32.1262 | 893.838
42735.0062 | 27.8243 | 32.1537 | 894.656
42750.0062 | 27.6562 | 28.9513 | 800.6852
42765.0062 | 27.6876 | 32.1595 | 890.4171
42780.0062 | 27.8179 | 32.0495 | 891.5495
42795.0062 | 27.818 | 32.1269 | 893.7078
42810.0062 | 27.8213 | 32.116 | 893.5094
42825.0062 | 27.8223 | 32.1118 | 893.4264
42840.0062 | 27.8232 | 32.1183 | 893.6351
42855.0062 | 27.8235 | 32.151 | 894.5511
42870.0062 | 27.8241 | 32.124 | 893.8242
42885.0062 | 27.8248 | 32.1235 | 893.8311
42900.0062 | 27.8239 | 32.1801 | 895.3743
42915.0062 | 27.8256 | 32.1718 | 895.1989
42930.0062 | 27.8262 | 32.1143 | 893.6185
42945.0062 | 27.8257 | 32.1338 | 894.1471
42960.0062 | 27.8261 | 32.0618 | 892.1538
42975.0062 | 27.8275 | 32.1278 | 894.0349
42990.0062 | 27.8278 | 32.1185 | 893.7881
43005.0062 | 27.8259 | 32.1316 | 894.0896
43020.0062 | 27.8265 | 32.1124 | 893.5783
43035.0062 | 27.8274 | 32.0778 | 892.6419
43050.0062 | 27.8276 | 32.0795 | 892.6953
43065.0062 | 27.8264 | 32.0749 | 892.5298
43080.0062 | 27.828 | 32.0962 | 893.1726
43095.0062 | 27.8279 | 32.1623 | 895.0109
43110.0062 | 27.8267 | 32.1174 | 893.7232
43125.0062 | 27.8271 | 32.0924 | 893.0373
43140.0062 | 27.8269 | 32.1212 | 893.8333
43155.0062 | 27.8293 | 32.0625 | 892.2789
43170.0062 | 27.8289 | 32.127 | 894.0583
43185.0062 | 27.8282 | 32.1233 | 893.9346
43200.0062 | 27.8284 | 32.0573 | 892.1017
43215.0062 | 27.8283 | 32.1376 | 894.3344
43230.0062 | 27.8297 | 32.1101 | 893.6142
43245.0062 | 27.8275 | 32.15 | 894.6569
43260.0062 | 27.8301 | 32.0556 | 892.1113
43275.0062 | 27.83 | 32.0854 | 892.935
43290.0062 | 27.8302 | 32.1291 | 894.1603
43305.0062 | 27.8271 | 32.1264 | 893.9835
43320.0062 | 27.8305 | 32.0797 | 892.7937
43335.0062 | 27.8303 | 32.0843 | 892.9154
43350.0062 | 27.7874 | 26.6883 | 741.5993
43365.0062 | 27.7003 | 26.9407 | 746.2652
43380.0062 | 27.8251 | 32.0947 | 893.0367
43395.0062 | 27.8274 | 32.0972 | 893.1815
43410.0062 | 27.8306 | 32.1583 | 894.986
43425.0062 | 27.8323 | 32.1442 | 894.6463
43440.0062 | 27.8313 | 32.1294 | 894.2021
43455.0062 | 27.8318 | 32.0897 | 893.116
43470.0062 | 27.8319 | 32.0505 | 892.0251
43485.0062 | 27.8305 | 32.1194 | 893.9002
43500.0062 | 27.8335 | 32.1091 | 893.708
43515.0062 | 27.8357 | 32.0692 | 892.6699
43530.0062 | 27.8355 | 32.1316 | 894.4007
43545.0062 | 27.8352 | 32.0668 | 892.5865
43560.0062 | 27.8341 | 32.0842 | 893.037
43575.0062 | 27.8334 | 32.085 | 893.0364
43590.0062 | 27.836 | 32.1028 | 893.6125
43605.0062 | 27.8359 | 32.0946 | 893.3814
43620.0062 | 27.8345 | 32.0815 | 892.9735
43635.0062 | 27.8365 | 32.1072 | 893.7522
43650.0062 | 27.8344 | 32.0554 | 892.2448
43665.0062 | 27.836 | 32.0516 | 892.1884
43680.0062 | 27.8355 | 32.136 | 894.522
43695.0062 | 27.8376 | 32.0663 | 892.6485
43710.0062 | 27.8351 | 32.1179 | 894.0061
43725.0062 | 27.8369 | 32.0569 | 892.365
43740.0062 | 27.8351 | 32.0348 | 891.6943
43755.0062 | 27.8371 | 32.1665 | 895.4223
43770.0062 | 27.8376 | 32.0215 | 891.4029
43785.0062 | 27.8361 | 32.0146 | 891.1626
43800.0062 | 27.839 | 32.0739 | 892.9036
43815.0062 | 27.8389 | 32.0622 | 892.5756
43830.0062 | 27.8392 | 32.02 | 891.4082
43845.0062 | 27.8407 | 32.0434 | 892.1131
43860.0062 | 27.8379 | 32.0762 | 892.9318
43875.0062 | 27.8374 | 32.056 | 892.356
43890.0062 | 27.8373 | 32.0657 | 892.6252
43905.0062 | 27.8405 | 32.0716 | 892.8866
43920.0062 | 27.8367 | 32.0617 | 892.4924
43935.0062 | 27.8399 | 32.0524 | 892.3332
43950.0062 | 27.779 | 27.0003 | 750.042
43965.0062 | 27.7051 | 26.8193 | 743.0328
43980.0062 | 27.8317 | 32.1281 | 894.1788
43995.0062 | 27.8342 | 32.0724 | 892.7089
44010.0062 | 27.8381 | 32.0958 | 893.4879
44025.0062 | 27.838 | 32.054 | 892.3175
44040.0062 | 27.8388 | 32.0717 | 892.8395
44055.0062 | 27.8383 | 32.0206 | 891.3989
44070.0062 | 27.84 | 32.0829 | 893.186
44085.0062 | 27.8402 | 32.0597 | 892.5483
44100.0062 | 27.8404 | 32.0861 | 893.2889
44115.0062 | 27.8409 | 32.1256 | 894.4073
44130.0062 | 27.842 | 32.1247 | 894.416
44145.0062 | 27.8393 | 32.0859 | 893.2499
44160.0062 | 27.8406 | 32.0611 | 892.6015
44175.0062 | 27.8433 | 32.0808 | 893.2332
44190.0062 | 27.8432 | 32.0672 | 892.8538
44205.0062 | 27.8424 | 32.1105 | 894.0332
44220.0062 | 27.8437 | 32.0707 | 892.9695
44235.0062 | 27.8426 | 32.0829 | 893.2713
44250.0062 | 27.8425 | 32.0684 | 892.8652
44265.0062 | 27.8443 | 32.0335 | 891.9486
44280.0062 | 27.8425 | 32.0688 | 892.8771
44295.0062 | 27.8427 | 32.0222 | 891.5855
44310.0062 | 27.843 | 32.0433 | 892.183
44325.0062 | 27.8463 | 32.0961 | 893.7561
44340.0062 | 27.845 | 32.0905 | 893.5605
44355.0062 | 27.8446 | 32.0847 | 893.3852
44370.0062 | 27.8456 | 31.9854 | 890.6527
44385.0062 | 27.845 | 32.0627 | 892.7868
44400.0062 | 27.8456 | 32.0456 | 892.3292
44415.0062 | 27.8441 | 32.0359 | 892.0117
44430.0062 | 27.8453 | 32.0067 | 891.2348
44445.0062 | 27.8459 | 31.9987 | 891.032
44460.0062 | 27.8462 | 32.0309 | 891.9369
44475.0062 | 27.8465 | 32.0265 | 891.8272
44490.0062 | 27.8462 | 32.1118 | 894.1896
44505.0062 | 27.8467 | 32.0432 | 892.2957
44520.0062 | 27.848 | 32.0889 | 893.6115
44535.0062 | 27.8495 | 32.0808 | 893.4329
44550.0062 | 27.7547 | 26.8692 | 745.7476
44565.0062 | 27.767 | 27.1929 | 755.0659
44580.0062 | 27.8428 | 32.086 | 893.366
44595.0062 | 27.8483 | 32.0952 | 893.7973
44610.0062 | 27.8481 | 32.0951 | 893.7886
44625.0062 | 27.8486 | 32.1017 | 893.9871
44640.0062 | 27.8483 | 32.0825 | 893.4423
44655.0062 | 27.8492 | 32.0865 | 893.5847
44670.0062 | 27.8499 | 32.1399 | 895.0925
44685.0062 | 27.8507 | 32.0512 | 892.649
44700.0062 | 27.853 | 32.091 | 893.8299
44715.0062 | 27.8532 | 32.0789 | 893.499
44730.0062 | 27.8534 | 32.116 | 894.5404
44745.0062 | 27.8518 | 31.9848 | 890.8336
44760.0062 | 27.8515 | 32.083 | 893.5575
44775.0062 | 27.8514 | 32.1113 | 894.3428
44790.0062 | 27.8523 | 32.0427 | 892.4614
44805.0062 | 27.8536 | 32.0467 | 892.6179
44820.0062 | 27.8555 | 31.9388 | 889.6706
44835.0062 | 27.8551 | 32.0415 | 892.5202
44850.0062 | 27.8553 | 32.0037 | 891.4709
44865.0062 | 27.8547 | 32.0268 | 892.097
44880.0062 | 27.8548 | 31.9934 | 891.1703
44895.0062 | 27.8549 | 32.0308 | 892.2157
44910.0062 | 27.8551 | 32.0271 | 892.1165
44925.0062 | 27.8567 | 31.9335 | 889.5621
44940.0062 | 27.8558 | 32.0674 | 893.2633
44955.0062 | 27.8564 | 32.0005 | 891.4202
44970.0062 | 27.8567 | 32.0892 | 893.8975
44985.0062 | 27.8564 | 32.0611 | 893.1066
45000.0062 | 27.8575 | 32.0892 | 893.9249
45015.0062 | 27.8592 | 32.0211 | 892.0814
45030.0062 | 27.8576 | 32.0887 | 893.9156
45045.0062 | 27.8571 | 32.0666 | 893.2839
45060.0062 | 27.8589 | 32.0942 | 894.109
45075.0062 | 27.8596 | 32.1078 | 894.5129
45090.0062 | 27.8602 | 32.0403 | 892.6478
45105.0062 | 27.8595 | 31.9628 | 890.4658
45120.0062 | 27.8615 | 32.0817 | 893.8427
45135.0062 | 27.8606 | 32.0454 | 892.8035
45150.0062 | 27.754 | 26.2511 | 728.5743
45165.0062 | 27.7795 | 26.9328 | 748.1804
45180.0062 | 27.8514 | 32.0462 | 892.5329
45195.0062 | 27.8566 | 32.0323 | 892.31
45210.0062 | 27.8581 | 32.1129 | 894.6042
45225.0062 | 27.8603 | 32.0282 | 892.3169
45240.0062 | 27.8573 | 32.1171 | 894.6946
45255.0062 | 27.8602 | 32.0129 | 891.887
45270.0062 | 27.8586 | 32.1235 | 894.918
45285.0062 | 27.8617 | 32.0982 | 894.3105
45300.0062 | 27.8605 | 32.0035 | 891.6339
45315.0062 | 27.863 | 32.0211 | 892.202
45330.0062 | 27.8625 | 32.1033 | 894.4797
45345.0062 | 27.8619 | 32.0986 | 894.3283
45360.0062 | 27.8641 | 32.0656 | 893.4811
45375.0062 | 27.8634 | 32.0251 | 892.3257
45390.0062 | 27.8615 | 32.072 | 893.5734
45405.0062 | 27.8629 | 32.0154 | 892.043
45420.0062 | 27.8631 | 32.0443 | 892.853
45435.0062 | 27.8629 | 32.0351 | 892.5901
45450.0062 | 27.8618 | 32.0831 | 893.8933
45465.0062 | 27.8662 | 31.9828 | 891.2367
45480.0062 | 27.8647 | 32.0878 | 894.1158
45495.0062 | 27.8641 | 32.0451 | 892.909
45510.0062 | 27.8644 | 32.0679 | 893.5519
45525.0062 | 27.864 | 31.9344 | 889.8225
45540.0062 | 27.8658 | 32.0676 | 893.59
45555.0062 | 27.8645 | 32.068 | 893.5592
45570.0062 | 27.8662 | 32.1195 | 895.0476
45585.0062 | 27.868 | 32.0314 | 892.6496
45600.0062 | 27.8681 | 32.0954 | 894.438
45615.0062 | 27.868 | 32.0929 | 894.3626
45630.0062 | 27.8672 | 32.0487 | 893.109
45645.0062 | 27.8678 | 32.122 | 895.1698
45660.0062 | 27.8685 | 32.0438 | 893.0112
45675.0062 | 27.8688 | 32.0432 | 893.0053
45690.0062 | 27.8695 | 32.0993 | 894.5898
45705.0062 | 27.8685 | 32.0292 | 892.6076
45720.0062 | 27.8712 | 32.1003 | 894.6755
45735.0062 | 27.8699 | 31.9998 | 891.8321
45750.0062 | 27.748 | 25.462 | 706.5206
45765.0062 | 27.8601 | 32.1361 | 895.3169
45780.0062 | 27.8653 | 32.0985 | 894.434
45795.0062 | 27.8688 | 32.0748 | 893.8839
45810.0062 | 27.8687 | 32.0464 | 893.0906
45825.0062 | 27.8682 | 32.08 | 894.0107
45840.0062 | 27.8701 | 31.9928 | 891.6409
45855.0062 | 27.869 | 32.0631 | 893.5663
45870.0062 | 27.8719 | 31.999 | 891.8718
45885.0062 | 27.8717 | 32.0934 | 894.4971
45900.0062 | 27.8721 | 32.0376 | 892.958
45915.0062 | 27.8714 | 32.0562 | 893.4525
45930.0062 | 27.8728 | 31.9995 | 891.9166
45945.0062 | 27.8732 | 32.0078 | 892.1594
45960.0062 | 27.8736 | 32.121 | 895.3281
45975.0062 | 27.8734 | 31.9966 | 891.8545
45990.0062 | 27.8731 | 32.0464 | 893.2313
46005.0062 | 27.8748 | 32.004 | 892.1054
46020.0062 | 27.8732 | 32.0382 | 893.0058
46035.0062 | 27.8732 | 32.0731 | 893.978
46050.0062 | 27.876 | 32.0545 | 893.5519
46065.0062 | 27.8736 | 31.9834 | 891.4921
46080.0062 | 27.8766 | 32.0183 | 892.5589
46095.0062 | 27.8764 | 32.1051 | 894.9744
46110.0062 | 27.8771 | 32.0518 | 893.5126
46125.0062 | 27.8752 | 32.086 | 894.4027
46140.0062 | 27.8785 | 32.0733 | 894.1535
46155.0062 | 27.8765 | 32.0697 | 893.9931
46170.0062 | 27.8766 | 32.0179 | 892.5499
46185.0062 | 27.8763 | 32.0627 | 893.7908
46200.0062 | 27.8763 | 32.0479 | 893.3771
46215.0062 | 27.8759 | 32.0581 | 893.6493
46230.0062 | 27.8787 | 32.0411 | 893.2641
46245.0062 | 27.8772 | 32.0614 | 893.7812
46260.0062 | 27.879 | 32.0745 | 894.2038
46275.0062 | 27.8787 | 31.9769 | 891.4723
46290.0062 | 27.8802 | 32.0626 | 893.9112
46305.0062 | 27.8783 | 32.0961 | 894.7844
46320.0062 | 27.8786 | 32.0551 | 893.6518
46335.0062 | 27.88 | 32.0524 | 893.6192
46350.0062 | 27.7395 | 26.8495 | 744.7919
46365.0062 | 27.8714 | 32.0097 | 892.155
46380.0062 | 27.8765 | 32.0608 | 893.7427
46395.0062 | 27.8775 | 32.0865 | 894.4919
46410.0062 | 27.878 | 32.0375 | 893.1412
46425.0062 | 27.8798 | 32.0988 | 894.9084
46440.0062 | 27.8804 | 32.0686 | 894.0846
46455.0062 | 27.8792 | 32.0809 | 894.3913
46470.0062 | 27.8833 | 32.107 | 895.2468
46485.0062 | 27.8809 | 31.9916 | 891.9552
46500.0062 | 27.8818 | 32.0315 | 893.0962
46515.0062 | 27.8806 | 31.9407 | 890.5235
46530.0062 | 27.8823 | 32.0624 | 893.9724
46545.0062 | 27.883 | 32.1119 | 895.3746
46560.0062 | 27.8848 | 32.0563 | 893.8855
46575.0062 | 27.8839 | 32.0946 | 894.9231
46590.0062 | 27.8846 | 32.0184 | 892.8201
46605.0062 | 27.8866 | 32.0247 | 893.0628
46620.0062 | 27.8837 | 32.1265 | 895.8053
46635.0062 | 27.8874 | 32.0237 | 893.0572
46650.0062 | 27.8846 | 32.0499 | 893.7001
46665.0062 | 27.8849 | 32.0738 | 894.3772
46680.0062 | 27.8859 | 32.0571 | 893.9394
46695.0062 | 27.8869 | 32.0025 | 892.4503
46710.0062 | 27.8872 | 31.9782 | 891.7818
46725.0062 | 27.8856 | 32.042 | 893.512
46740.0062 | 27.8887 | 32.0296 | 893.2663
46755.0062 | 27.8864 | 32.0127 | 892.721
46770.0062 | 27.8887 | 32.0419 | 893.6077
46785.0062 | 27.8903 | 32.0388 | 893.5694
46800.0062 | 27.8878 | 32.0951 | 895.0635
46815.0062 | 27.8884 | 32.0451 | 893.6856
46830.0062 | 27.8898 | 31.9896 | 892.183
46845.0062 | 27.8899 | 32.0537 | 893.9744
46860.0062 | 27.8869 | 32.0186 | 892.8997
46875.0062 | 27.8873 | 31.949 | 890.9693
46890.0062 | 27.8899 | 32.0222 | 893.0962
46905.0062 | 27.8906 | 32.0118 | 892.8285
46920.0062 | 27.888 | 32.0336 | 893.3539
46935.0062 | 27.8899 | 32.0372 | 893.5151
46950.0062 | 27.7442 | 27.5204 | 763.5305
46965.0062 | 27.7429 | 28.8509 | 800.4079
46980.0062 | 27.8843 | 31.994 | 892.1304
46995.0062 | 27.8904 | 31.9421 | 890.8774
47010.0062 | 27.8929 | 31.9865 | 892.1952
47025.0062 | 27.8944 | 31.9836 | 892.1635
47040.0062 | 27.893 | 32.0696 | 894.5175
47055.0062 | 27.8961 | 31.9572 | 891.4807
47070.0062 | 27.8944 | 32.0672 | 894.4947
47085.0062 | 27.8947 | 31.9784 | 892.0277
47100.0062 | 27.8973 | 32.008 | 892.9362
47115.0062 | 27.8978 | 32.0286 | 893.5275
47130.0062 | 27.8985 | 32.0303 | 893.5974
47145.0062 | 27.8997 | 32.0066 | 892.9735
47160.0062 | 27.8982 | 32.0342 | 893.6971
47175.0062 | 27.9001 | 32.073 | 894.8407
47190.0062 | 27.9019 | 31.9996 | 892.8472
47205.0062 | 27.8998 | 32.0192 | 893.3295
47220.0062 | 27.9005 | 32.0536 | 894.314
47235.0062 | 27.904 | 32.0373 | 893.968
47250.0062 | 27.9052 | 32.0369 | 893.9971
47265.0062 | 27.9032 | 32.0579 | 894.5186
47280.0062 | 27.9058 | 32.0062 | 893.1574
47295.0062 | 27.9047 | 31.9767 | 892.3017
47310.0062 | 27.9033 | 31.9925 | 892.6983
47325.0062 | 27.9031 | 32.0425 | 894.0862
47340.0062 | 27.9048 | 32.0148 | 893.3661
47355.0062 | 27.9042 | 32.057 | 894.5252
47370.0062 | 27.9039 | 32.0384 | 893.9944
47385.0062 | 27.904 | 31.968 | 892.0353
47400.0062 | 27.9026 | 31.9891 | 892.5773
47415.0062 | 27.9036 | 32.013 | 893.2767
47430.0062 | 27.9033 | 32.0264 | 893.6436
47445.0062 | 27.9038 | 32.0143 | 893.3202
47460.0062 | 27.9059 | 31.9919 | 892.7613
47475.0062 | 27.9042 | 31.9964 | 892.8357
47490.0062 | 27.9028 | 32.0645 | 894.6912
47505.0062 | 27.9043 | 32.0084 | 893.1724
47520.0062 | 27.9045 | 32.0423 | 894.1259
47535.0062 | 27.9063 | 32.008 | 893.223
47550.0062 | 27.7732 | 26.3924 | 733.002
47565.0062 | 27.8954 | 32.0291 | 893.4664
47580.0062 | 27.8983 | 32.0103 | 893.0341
47595.0062 | 27.9014 | 31.9792 | 892.2642
47610.0062 | 27.9058 | 31.9963 | 892.8818
47625.0062 | 27.9051 | 32.0252 | 893.666
47640.0062 | 27.9046 | 32.0426 | 894.1361
47655.0062 | 27.9059 | 32.0255 | 893.7
47670.0062 | 27.9057 | 32.0546 | 894.5057
47685.0062 | 27.9064 | 31.9369 | 891.2417
47700.0062 | 27.9075 | 31.9573 | 891.8478
47715.0062 | 27.9062 | 32.0609 | 894.6998
47730.0062 | 27.9083 | 32.0485 | 894.4211
47745.0062 | 27.9097 | 31.9265 | 891.0571
47760.0062 | 27.9096 | 32.0256 | 893.8232
47775.0062 | 27.9093 | 31.9876 | 892.7514
47790.0062 | 27.9059 | 32.0467 | 894.2942
47805.0062 | 27.9102 | 32.055 | 894.6623
47820.0062 | 27.9124 | 32.0467 | 894.4984
47835.0062 | 27.9118 | 31.9936 | 892.9983
47850.0062 | 27.9126 | 31.9941 | 893.0388
47865.0062 | 27.9118 | 31.9926 | 892.9715
47880.0062 | 27.9128 | 31.9904 | 892.9404
47895.0062 | 27.9135 | 31.9926 | 893.0256
47910.0062 | 27.9117 | 32.0246 | 893.8602
47925.0062 | 27.9142 | 31.9852 | 892.8409
47940.0062 | 27.9117 | 31.984 | 892.7276
47955.0062 | 27.9129 | 31.9789 | 892.6217
47970.0062 | 27.9135 | 32.0078 | 893.4497
47985.0062 | 27.9158 | 31.9981 | 893.2533
48000.0062 | 27.9142 | 31.9386 | 891.5399
48015.0062 | 27.9148 | 32.0214 | 893.8696
48030.0062 | 27.9156 | 31.9709 | 892.4875
48045.0062 | 27.916 | 31.9759 | 892.6406
48060.0062 | 27.9168 | 32.0157 | 893.7745
48075.0062 | 27.9169 | 31.9335 | 891.4866
48090.0062 | 27.916 | 32.0061 | 893.4821
48105.0062 | 27.9182 | 31.9952 | 893.2487
48120.0062 | 27.9175 | 31.9995 | 893.3451
48135.0062 | 27.9184 | 32.031 | 894.2548
48150.0062 | 27.7907 | 27.0901 | 752.8536
48165.0062 | 27.9095 | 32.0537 | 894.6016
48180.0062 | 27.915 | 32.0565 | 894.8577
48195.0062 | 27.916 | 31.95 | 891.9174
48210.0062 | 27.9187 | 32.0429 | 894.5967
48225.0062 | 27.9185 | 32.0382 | 894.4585
48240.0062 | 27.9192 | 32.0012 | 893.4495
48255.0062 | 27.9208 | 32.0128 | 893.8213
48270.0062 | 27.9206 | 31.9897 | 893.171
48285.0062 | 27.9217 | 32.0284 | 894.2895
48300.0062 | 27.9217 | 31.9801 | 892.9395
48315.0062 | 27.9203 | 32.0119 | 893.7805
48330.0062 | 27.9226 | 32.0325 | 894.4296
48345.0062 | 27.9228 | 31.9696 | 892.6822
48360.0062 | 27.9236 | 32.0188 | 894.0807
48375.0062 | 27.9232 | 31.9647 | 892.5585
48390.0062 | 27.9244 | 31.9921 | 893.3596
48405.0062 | 27.9252 | 31.9903 | 893.3337
48420.0062 | 27.9243 | 31.98 | 893.0177
48435.0062 | 27.925 | 31.9988 | 893.5665
48450.0062 | 27.9259 | 31.9632 | 892.5985
48465.0062 | 27.9245 | 31.9587 | 892.4322
48480.0062 | 27.928 | 32.0173 | 894.181
48495.0062 | 27.9278 | 31.9824 | 893.1977
48510.0062 | 27.9287 | 31.8631 | 889.8951
48525.0062 | 27.9284 | 31.9459 | 892.1985
48540.0062 | 27.93 | 32.0122 | 894.1017
48555.0062 | 27.9296 | 31.9353 | 891.9402
48570.0062 | 27.9297 | 32.0024 | 893.8153
48585.0062 | 27.9299 | 32.0499 | 895.1515
48600.0062 | 27.9306 | 31.9762 | 893.1138
48615.0062 | 27.9308 | 31.9082 | 891.221
48630.0062 | 27.932 | 31.9098 | 891.304
48645.0062 | 27.9322 | 31.958 | 892.6559
48660.0062 | 27.9313 | 31.9231 | 891.6542
48675.0062 | 27.9313 | 31.9174 | 891.494
48690.0062 | 27.9318 | 31.9339 | 891.971
48705.0062 | 27.9337 | 31.9433 | 892.2948
48720.0062 | 27.9331 | 31.9377 | 892.1195
48735.0062 | 27.9363 | 31.9584 | 892.7976
48750.0062 | 27.7981 | 26.8653 | 746.8033
48765.0062 | 27.9239 | 31.9265 | 891.5127
48780.0062 | 27.9307 | 31.9773 | 893.1488
48795.0062 | 27.9319 | 31.9405 | 892.1574
48810.0062 | 27.9367 | 32.0116 | 894.3005
48825.0062 | 27.9383 | 31.9686 | 893.1473
48840.0062 | 27.9396 | 32.006 | 894.2331
48855.0062 | 27.9394 | 31.9085 | 891.5034
48870.0062 | 27.9393 | 32.0095 | 894.3241
48885.0062 | 27.9413 | 32.0283 | 894.9104
48900.0062 | 27.9409 | 31.9722 | 893.33
48915.0062 | 27.941 | 31.9462 | 892.6087
48930.0062 | 27.9412 | 31.919 | 891.8569
48945.0062 | 27.942 | 31.9392 | 892.4463
48960.0062 | 27.9436 | 31.9361 | 892.4087
48975.0062 | 27.944 | 31.9921 | 893.9875
48990.0062 | 27.9441 | 31.8992 | 891.3951
49005.0062 | 27.9447 | 32.0369 | 895.26
49020.0062 | 27.9458 | 31.9686 | 893.3886
49035.0062 | 27.9463 | 31.9666 | 893.3488
49050.0062 | 27.9488 | 31.9743 | 893.6421
49065.0062 | 27.9468 | 31.9433 | 892.7107
49080.0062 | 27.9485 | 31.9414 | 892.7151
49095.0062 | 27.9489 | 31.9936 | 894.1861
49110.0062 | 27.9496 | 31.9407 | 892.7296
49125.0062 | 27.9492 | 31.9899 | 894.0902
49140.0062 | 27.9506 | 31.9882 | 894.0899
49155.0062 | 27.9491 | 31.9537 | 893.0749
49170.0062 | 27.9526 | 31.9857 | 894.0845
49185.0062 | 27.9525 | 32.0285 | 895.2777
49200.0062 | 27.953 | 31.9793 | 893.9159
49215.0062 | 27.9544 | 31.9779 | 893.9231
49230.0062 | 27.9554 | 31.978 | 893.958
49245.0062 | 27.9538 | 31.986 | 894.1295
49260.0062 | 27.9556 | 31.907 | 891.9794
49275.0062 | 27.9545 | 31.9789 | 893.9542
49290.0062 | 27.9574 | 31.968 | 893.7429
49305.0062 | 27.9569 | 32.0144 | 895.0232
49320.0062 | 27.9557 | 31.9816 | 894.0688
49335.0062 | 27.9594 | 31.8947 | 891.7572
49350.0062 | 27.8329 | 26.5155 | 738.0031
49365.0062 | 27.9524 | 31.9452 | 892.9457
49380.0062 | 27.9585 | 31.9091 | 892.1299
49395.0062 | 27.9621 | 31.9622 | 893.7313
49410.0062 | 27.963 | 32.0118 | 895.1446
49425.0062 | 27.9641 | 31.9552 | 893.5961
49440.0062 | 27.9643 | 31.9411 | 893.2105
49455.0062 | 27.9665 | 31.886 | 891.7379
49470.0062 | 27.9679 | 31.9069 | 892.3664
49485.0062 | 27.9692 | 31.9075 | 892.4253
49500.0062 | 27.9685 | 31.984 | 894.5469
49515.0062 | 27.971 | 31.9926 | 894.8652
49530.0062 | 27.9729 | 31.9938 | 894.9613
49545.0062 | 27.9731 | 31.9696 | 894.2869
49560.0062 | 27.9749 | 31.9497 | 893.7884
49575.0062 | 27.9728 | 31.8915 | 892.097
49590.0062 | 27.9726 | 31.8777 | 891.7011
49605.0062 | 27.9757 | 31.8954 | 892.2934
49620.0062 | 27.9761 | 31.8932 | 892.2454
49635.0062 | 27.9747 | 31.9311 | 893.2653
49650.0062 | 27.9785 | 31.9431 | 893.7191
49665.0062 | 27.9793 | 31.9415 | 893.703
49680.0062 | 27.9793 | 31.9397 | 893.6509
49695.0062 | 27.982 | 31.9719 | 894.6376
49710.0062 | 27.983 | 31.9606 | 894.3519
49725.0062 | 27.9834 | 31.8962 | 892.5639
49740.0062 | 27.9832 | 31.916 | 893.1134
49755.0062 | 27.9848 | 31.9658 | 894.5574
49770.0062 | 27.9829 | 31.8888 | 892.3397
49785.0062 | 27.9861 | 31.9171 | 893.2359
49800.0062 | 27.9841 | 31.9528 | 894.1693
49815.0062 | 27.9885 | 31.9442 | 894.0695
49830.0062 | 27.9887 | 31.9102 | 893.1244
49845.0062 | 27.9887 | 31.9438 | 894.0658
49860.0062 | 27.9901 | 31.9132 | 893.255
49875.0062 | 27.9912 | 31.9457 | 894.1976
49890.0062 | 27.9906 | 31.9 | 892.9008
49905.0062 | 27.9941 | 31.9428 | 894.2101
49920.0062 | 27.9935 | 31.8963 | 892.8914
49935.0062 | 27.9937 | 31.8653 | 892.027
49950.0062 | 27.8356 | 28.768 | 800.7723
49965.0062 | 27.8163 | 31.9231 | 887.9834
49980.0062 | 27.9864 | 31.895 | 892.6259
49995.0062 | 27.9921 | 31.9532 | 894.4372
50010.0062 | 27.9964 | 31.9368 | 894.1167
50025.0062 | 27.9984 | 31.923 | 893.7913
50040.0062 | 27.999 | 31.9347 | 894.1401
50055.0062 | 28 | 31.9177 | 893.6965
50070.0062 | 28.0035 | 31.8098 | 890.7878
50085.0062 | 28.0058 | 31.9129 | 893.7466
50100.0062 | 28.0067 | 31.902 | 893.4702
50115.0062 | 28.008 | 31.9601 | 895.1382
50130.0062 | 28.0085 | 31.9626 | 895.2256
50145.0062 | 28.009 | 31.8731 | 892.732
50160.0062 | 28.0108 | 31.8781 | 892.9301
50175.0062 | 28.013 | 31.8358 | 891.814
50190.0062 | 28.0157 | 31.9414 | 894.8587
50205.0062 | 28.0145 | 31.8577 | 892.4777
50220.0062 | 28.0158 | 31.8306 | 891.7606
50235.0062 | 28.02 | 31.8884 | 893.5129
50250.0062 | 28.0193 | 31.8411 | 892.1647
50265.0062 | 28.0189 | 31.8866 | 893.429
50280.0062 | 28.023 | 31.91 | 894.2129
50295.0062 | 28.0245 | 31.8953 | 893.8516
50310.0062 | 28.0249 | 31.9208 | 894.5794
50325.0062 | 28.0262 | 31.8469 | 892.5498
50340.0062 | 28.0264 | 31.8907 | 893.7809
50355.0062 | 28.0282 | 31.886 | 893.709
50370.0062 | 28.0315 | 31.7553 | 890.1471
50385.0062 | 28.0315 | 31.8673 | 893.2883
50400.0062 | 28.0338 | 31.8488 | 892.8427
50415.0062 | 28.0354 | 31.8401 | 892.6491
50430.0062 | 28.0378 | 31.8316 | 892.4878
50445.0062 | 28.0385 | 31.8475 | 892.9583
50460.0062 | 28.0404 | 31.8407 | 892.8261
50475.0062 | 28.0413 | 31.884 | 894.0692
50490.0062 | 28.0425 | 31.903 | 894.6415
50505.0062 | 28.0428 | 31.7723 | 890.9831
50520.0062 | 28.0478 | 31.8632 | 893.694
50535.0062 | 28.0466 | 31.9164 | 895.1493
50550.0062 | 27.9025 | 31.8592 | 888.9509
50565.0062 | 28.0451 | 31.8702 | 893.8035
50580.0062 | 28.0491 | 31.8856 | 894.3637
50595.0062 | 28.0523 | 31.8882 | 894.5363
50610.0062 | 28.0533 | 31.8266 | 892.8407
50625.0062 | 28.0583 | 31.9373 | 896.1072
50640.0062 | 28.0597 | 31.861 | 894.0114
50655.0062 | 28.0617 | 31.8403 | 893.4909
50670.0062 | 28.0618 | 31.8703 | 894.3381
50685.0062 | 28.0651 | 31.855 | 894.0129
50700.0062 | 28.0668 | 31.8084 | 892.7597
50715.0062 | 28.0704 | 31.8344 | 893.6054
50730.0062 | 28.0712 | 31.8114 | 892.9851
50745.0062 | 28.0739 | 31.8106 | 893.0483
50760.0062 | 28.0769 | 31.8172 | 893.3288
50775.0062 | 28.0777 | 31.8289 | 893.683
50790.0062 | 28.0796 | 31.7268 | 890.8756
50805.0062 | 28.0813 | 31.841 | 894.1361
50820.0062 | 28.0852 | 31.7981 | 893.0537
50835.0062 | 28.0877 | 31.8133 | 893.5621
50850.0062 | 28.0907 | 31.8196 | 893.8338
50865.0062 | 28.0933 | 31.8049 | 893.5053
50880.0062 | 28.0945 | 31.7969 | 893.3181
50895.0062 | 28.0956 | 31.8424 | 894.6312
50910.0062 | 28.1015 | 31.8375 | 894.681
50925.0062 | 28.1018 | 31.7206 | 891.4043
50940.0062 | 28.1054 | 31.7978 | 893.6903
50955.0062 | 28.1077 | 31.8431 | 895.0363
50970.0062 | 28.1125 | 31.7701 | 893.1363
50985.0062 | 28.1135 | 31.7653 | 893.0324
51000.0062 | 28.118 | 31.8156 | 894.5897
51015.0062 | 28.1203 | 31.7456 | 892.6972
51030.0062 | 28.1222 | 31.7218 | 892.087
51045.0062 | 28.1258 | 31.7415 | 892.7573
51060.0062 | 28.1307 | 31.8008 | 894.5799
51075.0062 | 28.1317 | 31.7901 | 894.3082
51090.0062 | 28.1348 | 31.7829 | 894.2082
51105.0062 | 28.1403 | 31.7496 | 893.4445
51120.0062 | 28.1429 | 31.7993 | 894.9241
51135.0062 | 28.1456 | 31.7438 | 893.4475
51150.0062 | 28.0218 | 31.7156 | 888.7274
51165.0062 | 28.1461 | 31.7287 | 893.0405
51180.0062 | 28.1525 | 31.7564 | 894.0208
51195.0062 | 28.1593 | 31.6269 | 890.5906
51210.0062 | 28.1601 | 31.7324 | 893.5891
51225.0062 | 28.1655 | 31.7683 | 894.7719
51240.0062 | 28.1724 | 31.6692 | 892.1947
51255.0062 | 28.1772 | 31.7396 | 894.3345
51270.0062 | 28.1819 | 31.7008 | 893.3911
51285.0062 | 28.186 | 31.7388 | 894.5911
51300.0062 | 28.1921 | 31.7634 | 895.4784
51315.0062 | 28.1951 | 31.6822 | 893.2826
51330.0062 | 28.2012 | 31.6427 | 892.3627
51345.0062 | 28.2068 | 31.7471 | 895.4838
51360.0062 | 28.214 | 31.6805 | 893.8356
51375.0062 | 28.2182 | 31.6081 | 891.9247
51390.0062 | 28.224 | 31.6176 | 892.3741
51405.0062 | 28.2297 | 31.5568 | 890.8385
51420.0062 | 28.2329 | 31.6358 | 893.1686
51435.0062 | 28.2398 | 31.5852 | 891.9569
51450.0062 | 28.2489 | 31.5761 | 891.9899
51465.0062 | 28.2554 | 31.6323 | 893.7843
51480.0062 | 28.2622 | 31.6404 | 894.2289
51495.0062 | 28.2686 | 31.5036 | 890.5632
51510.0062 | 28.2781 | 31.6116 | 893.9155
51525.0062 | 28.2831 | 31.5607 | 892.636
51540.0062 | 28.2923 | 31.558 | 892.8492
51555.0062 | 28.2981 | 31.571 | 893.3982
51570.0062 | 28.3115 | 31.5566 | 893.4147
51585.0062 | 28.319 | 31.5516 | 893.5122
51600.0062 | 28.3304 | 31.5268 | 893.1654
51615.0062 | 28.3383 | 31.5467 | 893.9811
51630.0062 | 28.35 | 31.5451 | 894.3046
51645.0062 | 28.3604 | 31.4493 | 891.916
51660.0062 | 28.3749 | 31.5317 | 894.7062
51675.0062 | 28.3855 | 31.4529 | 892.8074
51690.0062 | 28.4002 | 31.4394 | 892.8833
51705.0062 | 28.4097 | 31.4013 | 892.1023
51720.0062 | 28.4266 | 31.4819 | 894.9239
51735.0062 | 28.441 | 31.4457 | 894.3467
51750.0062 | 28.3239 | 27.092 | 767.3502
51765.0062 | 28.4028 | 31.4385 | 892.9418
51780.0062 | 28.4735 | 31.4217 | 894.6866
51795.0062 | 28.4961 | 31.2087 | 889.3275
51810.0062 | 28.5149 | 31.1141 | 887.2147
51825.0062 | 28.5312 | 30.7292 | 876.74
51840.0062 | 28.5183 | 29.8539 | 851.3818
51855.0062 | 28.5242 | 29.4577 | 840.2587
51870.0062 | 28.5303 | 29.0593 | 829.0693
51885.0062 | 28.5296 | 28.4577 | 811.8858
51900.0062 | 28.5351 | 28.0701 | 800.982
51915.0062 | 28.5414 | 27.6415 | 788.9272
51930.0062 | 28.5476 | 27.189 | 776.1809
51945.0062 | 28.5484 | 26.3706 | 752.8384
51960.0062 | 28.5551 | 26.0214 | 743.0421
51975.0062 | 28.5595 | 25.7077 | 734.1999
51990.0062 | 28.5644 | 25.2743 | 721.9454
52005.0062 | 28.5633 | 24.7675 | 707.4397
52020.0062 | 28.5697 | 24.3752 | 696.3911
52035.0062 | 28.5757 | 23.9843 | 685.3676
52050.0062 | 28.5805 | 23.2947 | 665.7725
52065.0062 | 28.5799 | 22.9669 | 656.3914
52080.0062 | 28.5854 | 22.5862 | 645.6347
52095.0062 | 28.5913 | 22.1608 | 633.605
52110.0062 | 28.5923 | 21.4855 | 614.3222
52125.0062 | 28.5968 | 21.127 | 604.1666
52140.0062 | 28.6026 | 20.7181 | 592.5917
52155.0062 | 28.6088 | 20.3229 | 581.415
52170.0062 | 28.6074 | 19.6607 | 562.4413
52185.0062 | 28.6129 | 19.2815 | 551.7014
52200.0062 | 28.6209 | 18.6778 | 534.5765
52215.0062 | 28.6253 | 9.1974 | 263.278
52230.0062 | 27.9978 | -0.0036577
52245.0062 | 27.8878 | -0.003535
52260.0062 | 27.8086 | -0.003537
52275.0062 | 27.7462 | -0.003533
52290.0062 | 27.6943 | -0.0035942
52305.0062 | 27.6496 | -0.003757
52320.0062 | 27.6104 | -0.0038165
52335.0062 | 27.5753 | -0.0037571
52350.0062 | 27.5436 | -0.0038374
52365.0062 | 27.5147 | -0.0037796
52380.0062 | 27.4882 | -0.0038148
52395.0062 | 27.4637 | -0.0039321
52410.0062 | 27.441 | -0.0040405
52425.0062 | 27.42 | -0.0041652
52440.0062 | 27.4002 | -0.0041681
52455.0062 | 27.3818 | -0.0041917
52470.0062 | 27.3644 | -0.0040248
52485.0062 | 27.3481 | -0.0040963
52500.0062 | 27.3327 | -0.0041714
52515.0062 | 27.3182 | -0.0042157
52530.0062 | 27.3043 | -0.0042245
52545.0062 | 27.2912 | -0.0041663
52560.0062 | 27.2787 | -0.0040593
52575.0062 | 27.2668 | -0.0041452
52590.0062 | 27.2555 | -0.0042527
52605.0062 | 27.2447 | -0.0042378
52620.0062 | 27.2343 | -0.0041901
52635.0062 | 27.2244 | -0.0041441
52650.0062 | 27.2149 | -0.0042452
52665.0062 | 27.2057 | -0.0043126
52680.0062 | 27.197 | -0.0042678
52695.0062 | 27.1886 | -0.0042521
52710.0062 | 27.1805 | -0.0042842
52725.0062 | 27.1727 | -0.00425
52740.0062 | 27.1652 | -0.0043492
52755.0062 | 27.158 | -0.0042734
52770.0062 | 27.151 | -0.0044131
52785.0062 | 27.1442 | -0.0043224
52800.0062 | 27.1377 | -0.0042678
52815.0062 | 27.1314 | -0.0042631
52830.0062 | 27.1253 | -0.0042727
52845.0062 | 27.1194 | -0.0043159
52860.0062 | 27.1137 | -0.0043085
52875.0062 | 27.1081 | -0.0043802
52890.0062 | 27.1027 | -0.0043293
52905.0062 | 27.0976 | -0.004325
52920.0062 | 27.0925 | -0.0042937
52935.0062 | 27.0876 | -0.0044091
52950.0062 | 27.0828 | -0.0044961
52965.0062 | 27.0782 | -0.0045081
52980.0062 | 27.0737 | -0.0045682
52995.0062 | 27.0693 | -0.0045985
53010.0062 | 27.0651 | -0.0046203
53025.0062 | 27.0609 | -0.0046696
53040.0062 | 27.0569 | -0.0047114
53055.0062 | 27.0529 | -0.0046788
53070.0062 | 27.0491 | -0.0048178
53085.0062 | 27.0454 | -0.0047567
53100.0062 | 27.0418 | -0.0047328
53115.0062 | 27.0382 | -0.0047504
53130.0062 | 27.0347 | -0.0047594
53145.0062 | 27.0313 | -0.0047603
53160.0062 | 27.028 | -0.0048229
53175.0062 | 27.0248 | -0.0047907
53190.0062 | 27.0216 | -0.0048102
53205.0062 | 27.0185 | -0.0047987
53220.0062 | 27.0155 | -0.0048469
53235.0062 | 27.0126 | -0.0049109
53250.0062 | 27.0097 | -0.00484
53265.0062 | 27.0069 | -0.0047526
53280.0062 | 27.0041 | -0.0048258
53295.0062 | 27.0014 | -0.0048563
53310.0062 | 26.9987 | -0.0048199
53325.0062 | 26.9961 | -0.0049124
53340.0062 | 26.9936 | -0.004917
53355.0062 | 26.9911 | -0.0048432
53370.0062 | 26.9886 | -0.0048571
53385.0062 | 26.9863 | -0.0047604
53400.0062 | 26.984 | -0.0048002
53415.0062 | 26.9816 | -0.0047301
53430.0062 | 26.9793 | -0.0047308
53445.0062 | 26.9771 | -0.004618
53460.0062 | 26.9749 | -0.0046928
53475.0062 | 26.9728 | -0.0047008
53490.0062 | 26.9708 | -0.0046716
53505.0062 | 26.9687 | -0.0045972
53520.0062 | 26.9667 | -0.0045909
53535.0062 | 26.9647 | -0.0044387
53550.0062 | 26.9627 | -0.0045554
53565.0062 | 26.9608 | -0.004489
53580.0062 | 26.959 | -0.0044756
53595.0062 | 26.9571 | -0.0044962
53610.0062 | 26.9552 | -0.0044443
53625.0062 | 26.9535 | -0.0045144
53640.0062 | 26.9517 | -0.0044285
53655.0062 | 26.95 | -0.0044146
53670.0062 | 26.9483 | -0.0044776
53685.0062 | 26.9466 | -0.0044392
53700.0062 | 26.945 | -0.0043279
53715.0062 | 26.9433 | -0.0044084
53730.0062 | 26.9417 | -0.0043616
53745.0062 | 26.9402 | -0.0043977
53760.0062 | 26.9386 | -0.004314
53775.0062 | 26.9371 | -0.0042596
53790.0062 | 26.9356 | -0.0042542
53805.0062 | 26.9341 | -0.0042587
53820.0062 | 26.9327 | -0.0042844
53835.0062 | 26.9313 | -0.0042171
53850.0062 | 26.9299 | -0.004265
53865.0062 | 26.9284 | -0.0043372
53880.0062 | 26.9271 | -0.0043021
53895.0062 | 26.9257 | -0.0043263
53910.0062 | 26.9244 | -0.0042961
53925.0062 | 26.9231 | -0.0043716
53940.0062 | 26.9218 | -0.0043691
53955.0062 | 26.9205 | -0.0043126
53970.0062 | 26.9192 | -0.0044261
53985.0062 | 26.918 | -0.0044325
54000.0062 | 26.9168 | -0.0043448
54015.0062 | 26.9156 | -0.0043432
54030.0062 | 26.9143 | -0.0044013
54045.0062 | 26.9132 | -0.0043865
54060.0062 | 26.912 | -0.0043067
54075.0062 | 26.9109 | -0.0043452
54090.0062 | 26.9097 | -0.0044057
54105.0062 | 26.9086 | -0.0043866
54120.0062 | 26.9075 | -0.0044673
54135.0062 | 26.9064 | -0.0044224
54150.0062 | 26.9054 | -0.004335
54165.0062 | 26.9043 | -0.0043222
54180.0062 | 26.9032 | -0.0042692
54195.0062 | 26.9022 | -0.0042971
54210.0062 | 26.9012 | -0.0042432
54225.0062 | 26.9002 | -0.0042594
54240.0062 | 26.8992 | -0.0042822
54255.0062 | 26.8982 | -0.0041811
54270.0062 | 26.8972 | -0.0042273
54285.0062 | 26.8962 | -0.0042949
54300.0062 | 26.8953 | -0.0042636
54315.0062 | 26.8943 | -0.0042871
54330.0062 | 26.8934 | -0.0042512
54345.0062 | 26.8925 | -0.0041476
54360.0062 | 26.8916 | -0.0042029
54375.0062 | 26.8907 | -0.0041704
54390.0062 | 26.8898 | -0.0041034
54405.0062 | 26.8889 | -0.004235
54420.0062 | 26.8881 | -0.0042359
54435.0062 | 26.8872 | -0.0042098
54450.0062 | 26.8863 | -0.0041834
54465.0062 | 26.8855 | -0.0041865
54480.0062 | 26.8846 | -0.0040704
54495.0062 | 26.8838 | -0.0040913
54510.0062 | 26.883 | -0.0041549
54525.0062 | 26.8822 | -0.004241
54540.0062 | 26.8814 | -0.0041777
54555.0062 | 26.8806 | -0.004117
54570.0062 | 26.8798 | -0.0041094
54585.0062 | 26.879 | -0.004073
54600.0062 | 26.8783 | -0.004151
54615.0062 | 26.8775 | -0.004168
54630.0062 | 26.8768 | -0.0041607
54645.0062 | 26.876 | -0.0041905
54660.0062 | 26.8753 | -0.0040678
54675.0062 | 26.8746 | -0.0040545
54690.0062 | 26.8738 | -0.0041502
54705.0062 | 26.8731 | -0.004162
54720.0062 | 26.8724 | -0.0039863
54735.0062 | 26.8718 | -0.0040312
54750.0062 | 26.871 | -0.0040695
54765.0062 | 26.8703 | -0.0040851
54780.0062 | 26.8697 | -0.0041003
54795.0062 | 26.869 | -0.0040291
54810.0062 | 26.8683 | -0.0040386
54825.0062 | 26.8676 | -0.0041137
54840.0062 | 26.867 | -0.0041367
54855.0062 | 26.8663 | -0.0041133
54870.0062 | 26.8657 | -0.0040835
54885.0062 | 26.8651 | -0.0040128
54900.0062 | 26.8644 | -0.0040159
54915.0062 | 26.8638 | -0.004003
54930.0062 | 26.8632 | -0.0039671
54945.0062 | 26.8626 | -0.0039536
54960.0062 | 26.862 | -0.0039762
54975.0062 | 26.8614 | -0.0039478
54990.0062 | 26.8608 | -0.0038611
55005.0062 | 26.8602 | -0.0039576
55020.0062 | 26.8596 | -0.003872
55035.0062 | 26.859 | -0.0039717
55050.0062 | 26.8584 | -0.0039838
55065.0062 | 26.8579 | -0.0038761
55080.0062 | 26.8573 | -0.0038945
55095.0062 | 26.8567 | -0.003874
55110.0062 | 26.8562 | -0.0039202
55125.0062 | 26.8556 | -0.0038548
55140.0062 | 26.8551 | -0.0038429
55155.0062 | 26.8546 | -0.0038344
55170.0062 | 26.854 | -0.0037778
55185.0062 | 26.8535 | -0.0038068
55200.0062 | 26.8529 | -0.0037902
55215.0062 | 26.8524 | -0.0038656
55230.0062 | 26.8519 | -0.0039136
55245.0062 | 26.8514 | -0.0037955
55260.0062 | 26.8509 | -0.0038043
55275.0062 | 26.8504 | -0.00397
55290.0062 | 26.8498 | -0.0039224
55305.0062 | 26.8493 | -0.0039288
55320.0062 | 26.8489 | -0.0037996
55335.0062 | 26.8484 | -0.0038406
55350.0062 | 26.8479 | -0.0040133
55365.0062 | 26.8474 | -0.0039855
55380.0062 | 26.8469 | -0.0039555
55395.0062 | 26.8464 | -0.0039003
55410.0062 | 26.846 | -0.0038788
55425.0062 | 26.8455 | -0.0039563
55440.0062 | 26.845 | -0.0039695
55455.0062 | 26.8445 | -0.0040015
55470.0062 | 26.8441 | -0.0039557
55485.0062 | 26.8436 | -0.0038702
55500.0062 | 26.8432 | -0.0039483
55515.0062 | 26.8427 | -0.0039145
55530.0062 | 26.8423 | -0.0038917
55545.0062 | 26.8418 | -0.0038247
55560.0062 | 26.8414 | -0.0038864
55575.0062 | 26.841 | -0.0039024
55590.0062 | 26.8406 | -0.0038625
55605.0062 | 26.8401 | -0.0038614
55620.0062 | 26.8397 | -0.0038344
55635.0062 | 26.8393 | -0.003749
55650.0062 | 26.8389 | -0.0038291
55665.0062 | 26.8385 | -0.0037887
55680.0062 | 26.838 | -0.0038875
55695.0062 | 26.8375 | -0.0038403
55710.0062 | 26.8371 | -0.0038528
55725.0062 | 26.8368 | -0.0038652
55740.0062 | 26.8364 | -0.0038187
55755.0062 | 26.8359 | -0.0037863
55770.0062 | 26.8356 | -0.0037281
55785.0062 | 26.8352 | -0.0038919
55800.0062 | 26.8348 | -0.0038024
55815.0062 | 26.8344 | -0.0038674
55830.0062 | 26.834 | -0.0037619
55845.0062 | 26.8336 | -0.0039121
55860.0062 | 26.8332 | -0.0038016
55875.0062 | 26.8329 | -0.0038881
55890.0062 | 26.8325 | -0.003859
55905.0062 | 26.8321 | -0.0038487
55920.0062 | 26.8318 | -0.0038073
55935.0062 | 26.8314 | -0.0037317
55950.0062 | 26.831 | -0.0037385
55965.0062 | 26.8306 | -0.0038039
55980.0062 | 26.8303 | -0.00366
55995.0062 | 26.8299 | -0.0037213
56010.0062 | 26.8296 | -0.0037318
56025.0062 | 26.8292 | -0.003732
56040.0062 | 26.8289 | -0.0036974
56055.0062 | 26.8286 | -0.0035359
56070.0062 | 26.8282 | -0.0037137
56085.0062 | 26.8278 | -0.0036265
56100.0062 | 26.8275 | -0.0037253
56115.0062 | 26.8272 | -0.0036832
56130.0062 | 26.8268 | -0.0036973
56145.0062 | 26.8265 | -0.0036745
56160.0062 | 26.8261 | -0.0036395
56175.0062 | 26.8258 | -0.0036735
56190.0062 | 26.8254 | -0.0036976
56205.0062 | 26.8251 | -0.003653
56220.0062 | 26.8248 | -0.0037299
56235.0062 | 26.8245 | -0.0035482
56250.0062 | 26.8241 | -0.0037108
56265.0062 | 26.8239 | -0.0036916
56280.0062 | 26.8236 | -0.0035837
56295.0062 | 26.8233 | -0.0036863
56310.0062 | 26.8229 | -0.0038059
56325.0062 | 26.8226 | -0.0038293
56340.0062 | 26.8223 | -0.0037152
56355.0062 | 26.822 | -0.0037061
56370.0062 | 26.8217 | -0.003735
56385.0062 | 26.8213 | -0.0037875
56400.0062 | 26.821 | -0.0037468
56415.0062 | 26.8207 | -0.0037974
56430.0062 | 26.8204 | -0.0037381
56445.0062 | 26.8202 | -0.0038407
56460.0062 | 26.8199 | -0.0038207
56475.0062 | 26.8196 | -0.0038929
56490.0062 | 26.8193 | -0.003917
56505.0062 | 26.819 | -0.0038283
56520.0062 | 26.8187 | -0.003872
56535.0062 | 26.8184 | -0.0039111
56550.0062 | 26.8181 | -0.0038092
56565.0062 | 26.8178 | -0.0037397
56580.0062 | 26.8175 | -0.0037757
56595.0062 | 26.8173 | -0.0037885
56610.0062 | 26.817 | -0.003879
56625.0062 | 26.8167 | -0.0038184
56640.0062 | 26.8164 | -0.0037853
56655.0062 | 26.8162 | -0.0037037
56670.0062 | 26.8159 | -0.003827
56685.0062 | 26.8156 | -0.0038451
56700.0062 | 26.8153 | -0.003795
56715.0062 | 26.8151 | -0.0037257
56730.0062 | 26.8148 | -0.0036824
56745.0062 | 26.8145 | -0.0037778
56760.0062 | 26.8142 | -0.0038103
56775.0062 | 26.814 | -0.0037437
56790.0062 | 26.8137 | -0.0037345
56805.0062 | 26.8135 | -0.0037463
56820.0062 | 26.8132 | -0.0037082
56835.0062 | 26.813 | -0.0037054
56850.0062 | 26.8127 | -0.003739
56865.0062 | 26.8125 | -0.0036887
56880.0062 | 26.8122 | -0.0037267
56895.0062 | 26.812 | -0.0037641
56910.0062 | 26.8117 | -0.0038801
56925.0062 | 26.8115 | -0.0037843
56940.0062 | 26.8112 | -0.003797
56955.0062 | 26.811 | -0.0038095
56970.0062 | 26.8107 | -0.0037881
56985.0062 | 26.8105 | -0.003728
57000.0062 | 26.8102 | -0.0036497
57015.0062 | 26.81 | -0.0037317
57030.0062 | 26.8097 | -0.0036813
57045.0062 | 26.8095 | -0.0036327
57060.0062 | 26.8093 | -0.0036365
57075.0062 | 26.809 | -0.0035994
57090.0062 | 26.8088 | -0.0036243
57105.0062 | 26.8085 | -0.0035547
57120.0062 | 26.8083 | -0.0035085
57135.0062 | 26.8081 | -0.0035053
57150.0062 | 26.8079 | -0.0035925
57165.0062 | 26.8076 | -0.0036501
57180.0062 | 26.8074 | -0.0035855
57195.0062 | 26.8072 | -0.003601
57210.0062 | 26.8069 | -0.0035822
57225.0062 | 26.8067 | -0.0036315
57240.0062 | 26.8065 | -0.0036061
57255.0062 | 26.8062 | -0.0036076
57270.0062 | 26.806 | -0.0036414
57285.0062 | 26.8058 | -0.0035704
57300.0062 | 26.8056 | -0.0036314
57315.0062 | 26.8054 | -0.0036292
57330.0062 | 26.8051 | -0.0036013
57345.0062 | 26.8049 | -0.0035844
57360.0062 | 26.8047 | -0.0036899
57375.0062 | 26.8045 | -0.0036977
57390.0062 | 26.8043 | -0.0035143
57405.0062 | 26.8041 | -0.0035436
57420.0062 | 26.8038 | -0.0036559
57435.0062 | 26.8036 | -0.0036285
57450.0062 | 26.8035 | -0.0037337
57465.0062 | 26.8032 | -0.0037654
57480.0062 | 26.803 | -0.0038055
57495.0062 | 26.8028 | -0.0038596
57510.0062 | 26.8026 | -0.0039477
57525.0062 | 26.8024 | -0.0039452
57540.0062 | 26.8022 | -0.0038256
57555.0062 | 26.802 | -0.003821
57570.0062 | 26.8019 | -0.0038758
57585.0062 | 26.8017 | -0.0038103
57600.0062 | 26.8014 | -0.0038493
57615.0062 | 26.8013 | -0.0038083
57630.0062 | 26.8011 | -0.0037693
57645.0062 | 26.8008 | -0.0038859
57660.0062 | 26.8007 | -0.0037766
57675.0062 | 26.8005 | -0.0038634
57690.0062 | 26.8003 | -0.0038138
57705.0062 | 26.8 | -0.0038134
57720.0062 | 26.7999 | -0.0037903
57735.0062 | 26.7997 | -0.0038604
57750.0062 | 26.7995 | -0.0038096
57765.0062 | 26.7993 | -0.0038735
57780.0062 | 26.7991 | -0.0037015
57795.0062 | 26.7989 | -0.0036896
57810.0062 | 26.7987 | -0.0038189
57825.0062 | 26.7985 | -0.0038254
57840.0062 | 26.7983 | -0.0037744
57855.0062 | 26.7981 | -0.0037568
57870.0062 | 26.798 | -0.003759
57885.0062 | 26.7978 | -0.0036857
57900.0062 | 26.7976 | -0.0036251
57915.0062 | 26.7974 | -0.003568
57930.0062 | 26.7973 | -0.0036325
57945.0062 | 26.797 | -0.0036057
57960.0062 | 26.7969 | -0.0036295
57975.0062 | 26.7967 | -0.0035744
57990.0062 | 26.7965 | -0.0035219
58005.0062 | 26.7963 | -0.0035511
58020.0062 | 26.7962 | -0.0035182
58035.0062 | 26.796 | -0.0035802
58050.0062 | 26.7958 | -0.0035546
58065.0062 | 26.7956 | -0.0035278
58080.0062 | 26.7954 | -0.0034512
58095.0062 | 26.7953 | -0.0034753
58110.0062 | 26.7951 | -0.0035297
58125.0062 | 26.7949 | -0.0035581
58140.0062 | 26.7948 | -0.0036614
58155.0062 | 26.7946 | -0.0036489
58170.0062 | 26.7944 | -0.0035619
58185.0062 | 26.7943 | -0.0035114
58200.0062 | 26.7941 | -0.0034365
58215.0062 | 26.7939 | -0.0034867
58230.0062 | 26.7937 | -0.0035518
58245.0062 | 26.7936 | -0.0036122
58260.0062 | 26.7934 | -0.0035865
58275.0062 | 26.7932 | -0.0035874
58290.0062 | 26.7931 | -0.0035355
58305.0062 | 26.7929 | -0.0035737
58320.0062 | 26.7928 | -0.0035463
58335.0062 | 26.7926 | -0.0035753
58350.0062 | 26.7925 | -0.003587
58365.0062 | 26.7923 | -0.0035812
58380.0062 | 26.7921 | -0.0035795
58395.0062 | 26.792 | -0.0035863
58410.0062 | 26.7918 | -0.0035662
58425.0062 | 26.7916 | -0.0036332
58440.0062 | 26.7915 | -0.0036901
58455.0062 | 26.7913 | -0.0037018
58470.0062 | 26.7912 | -0.0037562
58485.0062 | 26.791 | -0.0037467
58500.0062 | 26.7909 | -0.0037991
58515.0062 | 26.7908 | -0.0038064
58530.0062 | 26.7906 | -0.0038281
58545.0062 | 26.7905 | -0.0038264
58560.0062 | 26.7903 | -0.0038337
58575.0062 | 26.7901 | -0.0038785
58590.0062 | 26.79 | -0.003725
58605.0062 | 26.7898 | -0.0038038
58620.0062 | 26.7897 | -0.0038214
58635.0062 | 26.7895 | -0.0037982
58650.0062 | 26.7894 | -0.0038034
58665.0062 | 26.7892 | -0.0038725
58680.0062 | 26.789 | -0.0037429
58695.0062 | 26.7889 | -0.0038155
58710.0062 | 26.7888 | -0.0037747
58725.0062 | 26.7886 | -0.0038275
58740.0062 | 26.7885 | -0.0038696
58755.0062 | 26.7883 | -0.0038435
58770.0062 | 26.7882 | -0.0038452
58785.0062 | 26.788 | -0.0038184
58800.0062 | 26.7879 | -0.0037943
58815.0062 | 26.7878 | -0.0038294
58830.0062 | 26.7876 | -0.0037721
58845.0062 | 26.7875 | -0.0037686
58860.0062 | 26.7873 | -0.003786
58875.0062 | 26.7872 | -0.0037343
58890.0062 | 26.787 | -0.0037466
58905.0062 | 26.7869 | -0.0037935
58920.0062 | 26.7867 | -0.0036806
58935.0062 | 26.7866 | -0.0036267
58950.0062 | 26.7865 | -0.0036269
58965.0062 | 26.7864 | -0.0036215
58980.0062 | 26.7862 | -0.0036537
58995.0062 | 26.7861 | -0.0035424
59010.0062 | 26.7859 | -0.003582
59025.0062 | 26.7858 | -0.0035696
59040.0062 | 26.7857 | -0.0036216
59055.0062 | 26.7855 | -0.0035955
59070.0062 | 26.7854 | -0.0036139
59085.0062 | 26.7852 | -0.0036037
59100.0062 | 26.7851 | -0.0035735
59115.0062 | 26.785 | -0.0036048
59130.0062 | 26.7849 | -0.0035148
59145.0062 | 26.7847 | -0.0034797
59160.0062 | 26.7846 | -0.0035457
59175.0062 | 26.7845 | -0.0034799
59190.0062 | 26.7843 | -0.0035364
59205.0062 | 26.7842 | -0.0035336
59220.0062 | 26.784 | -0.0036095
59235.0062 | 26.7839 | -0.0036617
59250.0062 | 26.7838 | -0.003729
59265.0062 | 26.7837 | -0.0036635
59280.0062 | 26.7836 | -0.0036351
59295.0062 | 26.7835 | -0.0036288
59310.0062 | 26.7833 | -0.0037084
59325.0062 | 26.7832 | -0.0036554
59340.0062 | 26.783 | -0.0035915
59355.0062 | 26.7829 | -0.0036112
59370.0062 | 26.7828 | -0.003606
59385.0062 | 26.7827 | -0.0035878
59400.0062 | 26.7825 | -0.0036873
59415.0062 | 26.7824 | -0.0037657
59430.0062 | 26.7822 | -0.0037866
59445.0062 | 26.7821 | -0.003816
59460.0062 | 26.782 | -0.00396
59475.0062 | 26.7819 | -0.0039127
59490.0062 | 26.7818 | -0.0039301
59505.0062 | 26.7816 | -0.0039204
59520.0062 | 26.7815 | -0.0039505
59535.0062 | 26.7814 | -0.0039344
59550.0062 | 26.7813 | -0.0039237
59565.0062 | 26.7812 | -0.0038251
59580.0062 | 26.781 | -0.0039232
59595.0062 | 26.7809 | -0.0039243
59610.0062 | 26.7809 | -0.0039557
59625.0062 | 26.7807 | -0.0039008
59640.0062 | 26.7806 | -0.0039385
59655.0062 | 26.7805 | -0.0039251
59670.0062 | 26.7803 | -0.0039471
59685.0062 | 26.7802 | -0.0039251
59700.0062 | 26.7801 | -0.0039292
59715.0062 | 26.78 | -0.0038213
59730.0062 | 26.7799 | -0.0038998
59745.0062 | 26.7798 | -0.003871
59760.0062 | 26.7797 | -0.0038039
59775.0062 | 26.7795 | -0.0038971
59790.0062 | 26.7794 | -0.0038871
59805.0062 | 26.7793 | -0.0038224
59820.0062 | 26.7792 | -0.0038652
59835.0062 | 26.7791 | -0.0036812
59850.0062 | 26.779 | -0.0037855
59865.0062 | 26.7789 | -0.0036718
59880.0062 | 26.7787 | -0.003622
59895.0062 | 26.7786 | -0.0035762
59910.0062 | 26.7785 | -0.0036003
59925.0062 | 26.7784 | -0.0036864
59940.0062 | 26.7783 | -0.0035772
59955.0062 | 26.7782 | -0.0036101
59970.0062 | 26.7781 | -0.0035679
59985.0062 | 26.7779 | -0.003636
60000.0062 | 26.7779 | -0.0036688
60015.0062 | 26.7778 | -0.0035709
60030.0062 | 26.7776 | -0.0036542
60045.0062 | 26.7775 | -0.0036194
60060.0062 | 26.7774 | -0.003588
60075.0062 | 26.7773 | -0.0034939
60090.0062 | 26.7772 | -0.0035186
60105.0062 | 26.7771 | -0.0035028
60120.0062 | 26.777 | -0.0035478
60135.0062 | 26.7769 | -0.0035282

## data_wkndTrip
Runtime: Sat 10AM to Mon 8AM (~2 days)
Relative Time | CH101 | CH102 |  | P_15Ws | 687090.6916
| pvVoltage | pvCurrent | pvPower | P_Ws | 10306360.3737
0 | 26.6389 | -0.022817 | -0.60782 | P_Wm | 171772.6729
15.0062 | 26.6392 | -0.023077 | -0.61476 | P_Wh | 2862.8779
30.0062 | 26.6393 | -0.023707 | -0.63153 | P_kWh | 2.8629
45.0062 | 27.3459 | 27.2505 | 745.1903
60.0062 | 27.5236 | 27.2884 | 751.0752 | Percent used | 22.33%
75.0062 | 27.6613 | 32.2947 | 893.3134
90.0062 | 27.6796 | 32.1486 | 889.8593 | Solar_theoretical | 2700
105.0062 | 27.7024 | 32.1443 | 890.4743
120.0062 | 27.7234 | 32.1848 | 892.2705
135.0062 | 27.7431 | 32.1346 | 891.5137
150.0062 | 27.7582 | 32.1064 | 891.218
165.0062 | 27.7705 | 32.1023 | 891.497
180.0062 | 27.7809 | 32.0636 | 890.7561
195.0062 | 27.792 | 32.1065 | 892.3044
210.0062 | 27.7973 | 32.1475 | 893.6134
225.0062 | 27.8079 | 32.0946 | 892.4838
240.0062 | 27.8155 | 32.1097 | 893.1461
255.0062 | 27.8178 | 32.1192 | 893.4835
270.0062 | 27.8237 | 32.0836 | 892.6832
285.0062 | 27.8326 | 32.0262 | 891.3719
300.0062 | 27.8338 | 32.0437 | 891.8984
315.0062 | 27.839 | 32.0797 | 893.064
330.0062 | 27.8396 | 32.0818 | 893.1448
345.0062 | 27.8401 | 32.1019 | 893.7214
360.0062 | 27.847 | 32.022 | 891.7169
375.0062 | 27.8477 | 32.0081 | 891.3519
390.0061 | 27.8492 | 32.0119 | 891.5044
405.0062 | 27.8489 | 32.0195 | 891.7068
420.0062 | 27.8518 | 32.051 | 892.6789
435.0062 | 27.8533 | 32.0129 | 891.6646
450.0062 | 27.855 | 31.985 | 890.9411
465.0062 | 27.8558 | 31.9941 | 891.224
480.0062 | 27.8555 | 32.0659 | 893.2103
495.0062 | 27.8593 | 32.0069 | 891.6886
510.0062 | 27.8579 | 32.0547 | 892.9768
525.0062 | 27.8567 | 32.0368 | 892.4408
540.0062 | 27.8587 | 32.0222 | 892.0947
555.0062 | 27.8588 | 32.0875 | 893.9195
570.0062 | 27.8588 | 31.9745 | 890.7723
585.0062 | 27.86 | 32.022 | 892.131
600.0062 | 27.8611 | 32.0188 | 892.0772
615.0062 | 27.8615 | 32.0279 | 892.3465
630.0062 | 27.7106 | 26.0772 | 722.6151
645.0062 | 27.721 | 27.8297 | 771.4673
660.0062 | 27.8589 | 32.0655 | 893.3094
675.0062 | 27.8625 | 32.007 | 891.7949
690.0062 | 27.8622 | 32.0327 | 892.5007
705.0062 | 27.8633 | 32.0321 | 892.521
720.0062 | 27.8657 | 31.9568 | 890.4983
735.0062 | 27.8676 | 32.0326 | 892.6723
750.0062 | 27.866 | 32.0022 | 891.7713
765.0062 | 27.8665 | 32.0657 | 893.56
780.0062 | 27.8668 | 31.9372 | 889.988
795.0062 | 27.8669 | 32.0002 | 891.7445
810.0062 | 27.8677 | 31.997 | 891.6838
825.0062 | 27.8658 | 32.0281 | 892.4889
840.0062 | 27.8659 | 32.0012 | 891.7437
855.0062 | 27.8675 | 31.9843 | 891.3235
870.0061 | 27.8686 | 32.0207 | 892.3718
885.0062 | 27.8669 | 32.0607 | 893.431
900.0062 | 27.8678 | 31.9342 | 889.9361
915.0062 | 27.8671 | 31.9601 | 890.6354
930.0062 | 27.8687 | 32.0153 | 892.2243
945.0062 | 27.8683 | 32.0359 | 892.784
960.0062 | 27.8681 | 31.9795 | 891.2086
975.0062 | 27.8686 | 32.0211 | 892.3847
990.0062 | 27.8689 | 31.9699 | 890.9659
1005.0062 | 27.8691 | 31.9849 | 891.391
1020.0062 | 27.8669 | 32.0153 | 892.1654
1035.0062 | 27.8688 | 31.9857 | 891.4054
1050.0061 | 27.8699 | 32.0389 | 892.9215
1065.0062 | 27.8682 | 32.015 | 892.2005
1080.0062 | 27.8686 | 31.9685 | 890.9167
1095.0062 | 27.8688 | 32.0542 | 893.3134
1110.0062 | 27.8675 | 31.9539 | 890.4734
1125.0062 | 27.8687 | 32.0311 | 892.6652
1140.0062 | 27.8673 | 31.9857 | 891.3553
1155.0062 | 27.869 | 32.0202 | 892.3713
1170.0062 | 27.8701 | 31.968 | 890.9514
1185.0062 | 27.8676 | 31.9678 | 890.8653
1200.0062 | 27.8666 | 32.043 | 892.9312
1215.0062 | 27.8676 | 31.9931 | 891.5723
1230.0062 | 27.74 | 27.6444 | 766.8565
1245.0062 | 27.865 | 32.0596 | 893.3417
1260.0062 | 27.8683 | 32.0266 | 892.5283
1275.0062 | 27.8659 | 31.9447 | 890.1684
1290.0062 | 27.8666 | 32.0995 | 894.504
1305.0062 | 27.8698 | 31.9733 | 891.0914
1320.0062 | 27.8671 | 31.9838 | 891.2964
1335.0062 | 27.868 | 31.9474 | 890.3081
1350.0062 | 27.868 | 32.0328 | 892.689
1365.0062 | 27.8668 | 32.0082 | 891.9662
1380.0062 | 27.8687 | 31.9506 | 890.422
1395.0062 | 27.8698 | 32.0292 | 892.6479
1410.0062 | 27.867 | 32.0428 | 892.9378
1425.0062 | 27.8655 | 31.9895 | 891.4014
1440.0062 | 27.8676 | 31.957 | 890.5652
1455.0062 | 27.8684 | 32.0511 | 893.212
1470.0062 | 27.8689 | 31.9697 | 890.9604
1485.0062 | 27.866 | 31.9815 | 891.1969
1500.0062 | 27.8644 | 32.0004 | 891.6726
1515.0062 | 27.8662 | 32.079 | 893.9213
1530.0062 | 27.8667 | 32.0108 | 892.0347
1545.0062 | 27.868 | 31.8988 | 888.9543
1560.0062 | 27.8652 | 32.0167 | 892.151
1575.0061 | 27.8648 | 32.0261 | 892.4012
1590.0062 | 27.8652 | 32.0012 | 891.7193
1605.0062 | 27.867 | 32.0208 | 892.3249
1620.0062 | 27.8677 | 31.9127 | 889.3346
1635.0062 | 27.8673 | 31.9841 | 891.3111
1650.0062 | 27.8672 | 31.9863 | 891.3681
1665.0062 | 27.8673 | 32.0272 | 892.5131
1680.0062 | 27.8661 | 32.0442 | 892.9477
1695.0062 | 27.8669 | 32.0917 | 894.2963
1710.0062 | 27.8654 | 32.0258 | 892.4139
1725.0062 | 27.8646 | 32.0206 | 892.2433
1740.0062 | 27.8657 | 31.9886 | 891.385
1755.0062 | 27.8656 | 32.0557 | 893.2502
1770.0061 | 27.8649 | 32.0092 | 891.9315
1785.0062 | 27.8654 | 31.9619 | 890.6328
1800.0062 | 27.8653 | 31.9876 | 891.3452
1815.0062 | 27.8658 | 32.0559 | 893.2644
1830.0062 | 27.733 | 27.3945 | 759.7309
1845.0062 | 27.7241 | 29.4638 | 816.8571
1860.0062 | 27.8606 | 32.0745 | 893.615
1875.0061 | 27.8627 | 31.9931 | 891.414
1890.0061 | 27.8651 | 32.1075 | 894.6801
1905.0062 | 27.8643 | 32.0255 | 892.3691
1920.0062 | 27.8633 | 32.0158 | 892.0684
1935.0062 | 27.8665 | 32.0376 | 892.7743
1950.0062 | 27.8654 | 32.0197 | 892.24
1965.0061 | 27.8641 | 32.0917 | 894.2049
1980.0062 | 27.8658 | 32.0243 | 892.3847
1995.0062 | 27.8664 | 31.973 | 890.9747
2010.0062 | 27.8655 | 32.0247 | 892.3852
2025.0062 | 27.864 | 31.9994 | 891.6318
2040.0062 | 27.864 | 31.9877 | 891.3074
2055.0062 | 27.8635 | 32.0983 | 894.3706
2070.0062 | 27.8664 | 32.0192 | 892.26
2085.0062 | 27.8657 | 31.9981 | 891.6499
2100.0062 | 27.8644 | 32.0138 | 892.0436
2115.0062 | 27.8653 | 32.0086 | 891.9287
2130.0062 | 27.8636 | 32.0113 | 891.9477
2145.0062 | 27.8627 | 32.0471 | 892.9199
2160.0062 | 27.8638 | 32.0459 | 892.9222
2175.0062 | 27.8642 | 31.9676 | 890.7515
2190.0061 | 27.8646 | 32.0803 | 893.9029
2205.0062 | 27.8647 | 32.0419 | 892.8371
2220.0062 | 27.866 | 32.049 | 893.0776
2235.0061 | 27.8634 | 31.9318 | 889.7276
2250.0062 | 27.8628 | 32.0022 | 891.6695
2265.0062 | 27.8625 | 31.9839 | 891.1521
2280.0062 | 27.8638 | 32.0351 | 892.6207
2295.0061 | 27.8614 | 32.0059 | 891.7273
2310.0061 | 27.8594 | 32.1187 | 894.8083
2325.0062 | 27.8651 | 32.1228 | 895.105
2340.0061 | 27.8645 | 32.0416 | 892.8251
2355.0061 | 27.863 | 32.0323 | 892.5152
2370.0062 | 27.8625 | 32.0042 | 891.7149
2385.0062 | 27.8623 | 32.089 | 894.0748
2400.0062 | 27.8628 | 32.043 | 892.8075
2415.0062 | 27.8628 | 31.9544 | 890.339
2430.0062 | 27.7185 | 28.2805 | 783.8935
2445.0062 | 27.7212 | 30.5546 | 847.0094
2460.0062 | 27.8582 | 32.0183 | 891.9713
2475.0062 | 27.8598 | 32.0098 | 891.786
2490.0061 | 27.8603 | 32.0914 | 894.0763
2505.0061 | 27.8617 | 31.9251 | 889.4876
2520.0062 | 27.8623 | 32.0235 | 892.2476
2535.0062 | 27.8599 | 32.0864 | 893.9244
2550.0062 | 27.8599 | 32.0033 | 891.6085
2565.0062 | 27.8603 | 32.0234 | 892.1808
2580.0062 | 27.8611 | 31.9921 | 891.336
2595.0062 | 27.8616 | 32.0485 | 892.9209
2610.0062 | 27.8603 | 31.9965 | 891.4305
2625.0062 | 27.8622 | 32.02 | 892.1479
2640.0062 | 27.8625 | 31.9705 | 890.7766
2655.0062 | 27.8614 | 32.0537 | 893.0617
2670.0062 | 27.8608 | 31.8965 | 888.6632
2685.0061 | 27.8629 | 31.9184 | 889.3401
2700.0062 | 27.8617 | 32.1093 | 894.6192
2715.0062 | 27.8602 | 32.04 | 892.6382
2730.0062 | 27.8604 | 32.0708 | 893.5059
2745.0062 | 27.8604 | 32.0218 | 892.1393
2760.0061 | 27.8626 | 32.0586 | 893.2367
2775.0062 | 27.8609 | 32.0374 | 892.5914
2790.0062 | 27.861 | 32.0789 | 893.749
2805.0062 | 27.8596 | 32.038 | 892.5654
2820.0062 | 27.86 | 32.1425 | 895.4881
2835.0062 | 27.8615 | 32.0657 | 893.3989
2850.0061 | 27.8611 | 32.0279 | 892.3321
2865.0062 | 27.8609 | 32.0418 | 892.712
2880.0061 | 27.8626 | 32.0497 | 892.986
2895.0062 | 27.8627 | 32.0422 | 892.7826
2910.0062 | 27.859 | 32.0586 | 893.1202
2925.0061 | 27.861 | 32.0507 | 892.965
2940.0062 | 27.859 | 32.0928 | 894.0736
2955.0061 | 27.8596 | 32.0454 | 892.7707
2970.0062 | 27.8611 | 32.0852 | 893.9294
2985.0061 | 27.8611 | 31.9978 | 891.4928
3000.0062 | 27.8612 | 32.0432 | 892.7626
3015.0062 | 27.8604 | 32.0543 | 893.0448
3030.0061 | 27.6922 | 29.4217 | 814.7521
3045.0062 | 27.6855 | 32.0691 | 887.8493
3060.0061 | 27.8565 | 32.0838 | 893.74
3075.0061 | 27.8591 | 32.0842 | 893.8365
3090.0062 | 27.8575 | 32.088 | 893.8902
3105.0062 | 27.8597 | 31.989 | 891.2056
3120.0062 | 27.86 | 32.0049 | 891.6568
3135.0062 | 27.8605 | 32.0061 | 891.7063
3150.0061 | 27.8599 | 32.0074 | 891.7221
3165.0062 | 27.8601 | 32.0213 | 892.1167
3180.0062 | 27.8588 | 32.0416 | 892.6397
3195.0062 | 27.8588 | 32.0907 | 894.0072
3210.0062 | 27.859 | 32.0432 | 892.692
3225.0062 | 27.8595 | 31.9874 | 891.1528
3240.0062 | 27.8596 | 32.073 | 893.5419
3255.0062 | 27.8592 | 32.0469 | 892.802
3270.0061 | 27.8564 | 31.9828 | 890.9246
3285.0061 | 27.8596 | 32.0789 | 893.7051
3300.0062 | 27.8591 | 32.063 | 893.2438
3315.0062 | 27.8576 | 32.0524 | 892.9024
3330.0061 | 27.8583 | 32.1038 | 894.3582
3345.0062 | 27.8604 | 32.0411 | 892.6782
3360.0062 | 27.859 | 32.103 | 894.3557
3375.0062 | 27.8583 | 32.0671 | 893.3358
3390.0062 | 27.8598 | 32.0019 | 891.5648
3405.0062 | 27.8597 | 32.1213 | 894.8907
3420.0062 | 27.8586 | 32.0099 | 891.7531
3435.0062 | 27.8569 | 32.1133 | 894.5771
3450.0062 | 27.8591 | 32.0597 | 893.1538
3465.0062 | 27.8581 | 32.0252 | 892.1611
3480.0062 | 27.8571 | 32.0715 | 893.4193
3495.0062 | 27.858 | 31.9803 | 890.9061
3510.0062 | 27.8596 | 32.0334 | 892.4397
3525.0062 | 27.8588 | 32.0856 | 893.8679
3540.0061 | 27.8583 | 32.06 | 893.1392
3555.0061 | 27.858 | 32.023 | 892.0975
3570.0062 | 27.8577 | 32.0539 | 892.95
3585.0062 | 27.8571 | 32.0806 | 893.6727
3600.0061 | 27.8578 | 32.0948 | 894.0889
3615.0062 | 27.8573 | 32.0709 | 893.4109
3630.0062 | 27.692 | 29.4542 | 815.644
3645.0062 | 27.6935 | 32.0492 | 887.5551
3660.0061 | 27.853 | 32.0821 | 893.5843
3675.0061 | 27.8554 | 32.0815 | 893.6442
3690.0062 | 27.8566 | 32.0042 | 891.5288
3705.0061 | 27.8576 | 32.0365 | 892.4576
3720.0061 | 27.8564 | 31.9948 | 891.258
3735.0061 | 27.8567 | 32.1408 | 895.338
3750.0062 | 27.8555 | 32.0115 | 891.6967
3765.0061 | 27.8566 | 32.0663 | 893.2588
3780.0061 | 27.8568 | 32.005 | 891.5565
3795.0062 | 27.8582 | 32.0488 | 892.8234
3810.0062 | 27.8566 | 32.0168 | 891.8792
3825.0062 | 27.8565 | 32.033 | 892.3288
3840.0062 | 27.8564 | 32.0576 | 893.0099
3855.0061 | 27.8558 | 32.0323 | 892.2876
3870.0062 | 27.8576 | 32.0676 | 893.3265
3885.0062 | 27.858 | 32.0403 | 892.5772
3900.0061 | 27.8579 | 32.0839 | 893.7925
3915.0061 | 27.8577 | 32.0849 | 893.8092
3930.0062 | 27.8566 | 32.1381 | 895.2582
3945.0062 | 27.8569 | 32.0492 | 892.7909
3960.0062 | 27.8576 | 32.06 | 893.1139
3975.0061 | 27.8556 | 32.0478 | 892.711
3990.0062 | 27.8584 | 32.0546 | 892.9883
4005.0062 | 27.857 | 31.9932 | 891.2347
4020.0062 | 27.8569 | 32.0572 | 893.012
4035.0061 | 27.8561 | 32.0482 | 892.7378
4050.0061 | 27.8579 | 32.0746 | 893.5294
4065.0062 | 27.857 | 32.1226 | 894.8413
4080.0062 | 27.8564 | 32.0565 | 892.9773
4095.0061 | 27.8577 | 32.0854 | 893.8237
4110.0061 | 27.8579 | 32.0603 | 893.1314
4125.0061 | 27.8573 | 32.039 | 892.5196
4140.0062 | 27.8578 | 31.9992 | 891.4286
4155.0061 | 27.8572 | 32.0307 | 892.2843
4170.0061 | 27.8556 | 32.0351 | 892.3559
4185.0062 | 27.8574 | 32.1162 | 894.6724
4200.0062 | 27.8584 | 32.0312 | 892.3378
4215.0062 | 27.8564 | 32.0821 | 893.6938
4230.0062 | 27.7187 | 30.0727 | 833.5745
4245.0062 | 27.8568 | 32.0214 | 892.0132
4260.0062 | 27.858 | 32.0916 | 894.0078
4275.0062 | 27.8569 | 31.9996 | 891.4098
4290.0062 | 27.8591 | 32.1015 | 894.3169
4305.0061 | 27.8561 | 32.08 | 893.6221
4320.0061 | 27.8565 | 32.0542 | 892.9171
4335.0062 | 27.8572 | 31.9777 | 890.8106
4350.0062 | 27.8569 | 32.043 | 892.6174
4365.0062 | 27.8583 | 32.0711 | 893.4472
4380.0062 | 27.8571 | 31.9748 | 890.7241
4395.0062 | 27.86 | 32.0087 | 891.7605
4410.0061 | 27.8578 | 31.985 | 891.0332
4425.0062 | 27.8582 | 32.038 | 892.5186
4440.0062 | 27.8561 | 32.0593 | 893.0461
4455.0062 | 27.8575 | 32.0336 | 892.3764
4470.0061 | 27.8569 | 32.077 | 893.5652
4485.0062 | 27.8568 | 32.0071 | 891.6148
4500.0062 | 27.8579 | 32.052 | 892.9027
4515.0061 | 27.8579 | 32.0421 | 892.6282
4530.0061 | 27.8584 | 32.0554 | 893.0126
4545.0062 | 27.8589 | 32.0748 | 893.5684
4560.0061 | 27.8587 | 31.9486 | 890.0452
4575.0061 | 27.8572 | 32.0165 | 891.8896
4590.0062 | 27.8577 | 31.9946 | 891.2978
4605.0062 | 27.8579 | 32.0872 | 893.8801
4620.0062 | 27.8566 | 32.1235 | 894.8526
4635.0062 | 27.8573 | 32.0811 | 893.6934
4650.0062 | 27.8588 | 32.0335 | 892.4129
4665.0061 | 27.8585 | 32.0136 | 891.8529
4680.0062 | 27.8582 | 32.0356 | 892.4524
4695.0062 | 27.8561 | 32.141 | 895.3247
4710.0062 | 27.8589 | 31.9853 | 891.0773
4725.0061 | 27.8582 | 32.0533 | 892.9463
4740.0062 | 27.857 | 32.0771 | 893.5731
4755.0061 | 27.8563 | 32.0687 | 893.3167
4770.0061 | 27.856 | 32.0224 | 892.0157
4785.0061 | 27.8562 | 31.9845 | 890.9661
4800.0061 | 27.8559 | 32.0874 | 893.8234
4815.0062 | 27.8558 | 32.0446 | 892.6293
4830.0061 | 27.701 | 29.0144 | 803.7293
4845.0061 | 27.8502 | 32.0546 | 892.7266
4860.0062 | 27.8542 | 32.0919 | 893.8921
4875.0062 | 27.8553 | 32.1049 | 894.2909
4890.0061 | 27.854 | 31.9767 | 890.6795
4905.0062 | 27.8527 | 32.1249 | 894.7627
4920.0062 | 27.8549 | 32.0654 | 893.1796
4935.0062 | 27.8553 | 32.1254 | 894.8645
4950.0062 | 27.8559 | 32.0156 | 891.8228
4965.0062 | 27.8521 | 32.0523 | 892.7266
4980.0061 | 27.8549 | 32.1005 | 894.1565
4995.0062 | 27.8541 | 32.1377 | 895.1695
5010.0062 | 27.8517 | 32.0921 | 893.8192
5025.0062 | 27.853 | 32.0645 | 893.094
5040.0061 | 27.8532 | 32.0875 | 893.7411
5055.0062 | 27.8521 | 32.0329 | 892.1853
5070.0061 | 27.8524 | 32.0293 | 892.0942
5085.0061 | 27.8527 | 32.0235 | 891.9402
5100.0062 | 27.8515 | 32.1277 | 894.8046
5115.0062 | 27.8532 | 32.05 | 892.6963
5130.0061 | 27.8515 | 32.0664 | 893.0979
5145.0061 | 27.8547 | 32.0143 | 891.7498
5160.0062 | 27.8528 | 32.0077 | 891.5043
5175.0061 | 27.8546 | 32.1089 | 894.3791
5190.0062 | 27.8519 | 32.0653 | 893.0798
5205.0062 | 27.8535 | 32.0186 | 891.8289
5220.0062 | 27.8545 | 32.0575 | 892.9433
5235.0062 | 27.8522 | 32.0693 | 893.1979
5250.0062 | 27.8534 | 32.0565 | 892.8827
5265.0062 | 27.8507 | 32.0942 | 893.8466
5280.0062 | 27.8523 | 32.0237 | 891.9316
5295.0062 | 27.8511 | 32.1189 | 894.5465
5310.0062 | 27.8513 | 32.085 | 893.6085
5325.0062 | 27.8537 | 32.1257 | 894.8215
5340.0062 | 27.855 | 31.977 | 890.7187
5355.0061 | 27.8546 | 32.0801 | 893.579
5370.0062 | 27.8548 | 32.0516 | 892.7918
5385.0062 | 27.8564 | 32.0285 | 892.1994
5400.0062 | 27.8572 | 32.0591 | 893.0787
5415.0062 | 27.8532 | 32.0626 | 893.048
5430.0062 | 27.6792 | 29.2042 | 808.3505
5445.0062 | 27.8477 | 32.0535 | 892.6171
5460.0061 | 27.8512 | 32.0872 | 893.6664
5475.0062 | 27.8529 | 31.9951 | 891.1571
5490.0062 | 27.8531 | 32.0631 | 893.0582
5505.0062 | 27.8543 | 32.0809 | 893.5914
5520.0062 | 27.8544 | 32.0908 | 893.8696
5535.0062 | 27.8558 | 32.0755 | 893.4905
5550.0062 | 27.8549 | 32.0556 | 892.9046
5565.0062 | 27.8551 | 32.1035 | 894.2471
5580.0062 | 27.8532 | 32.0602 | 892.982
5595.0062 | 27.8566 | 32.0791 | 893.6154
5610.0061 | 27.8581 | 32.0374 | 892.5033
5625.0062 | 27.8571 | 32.0842 | 893.7745
5640.0062 | 27.8576 | 32.0925 | 894.0223
5655.0062 | 27.8563 | 32.0584 | 893.0272
5670.0062 | 27.8539 | 32.0325 | 892.23
5685.0062 | 27.8543 | 32.0566 | 892.9152
5700.0061 | 27.8554 | 32.0586 | 893.0045
5715.0061 | 27.8527 | 32.1018 | 894.1207
5730.0062 | 27.8521 | 32.0806 | 893.511
5745.0062 | 27.855 | 32.088 | 893.8135
5760.0061 | 27.8542 | 32.0049 | 891.4707
5775.0061 | 27.8525 | 31.9791 | 890.6962
5790.0062 | 27.8526 | 32.0919 | 893.8414
5805.0062 | 27.8545 | 32.0432 | 892.5472
5820.0062 | 27.8534 | 32.1112 | 894.4069
5835.0062 | 27.8534 | 32.0941 | 893.9321
5850.0062 | 27.8545 | 31.9402 | 889.6795
5865.0062 | 27.8526 | 32.0067 | 891.4706
5880.0061 | 27.8547 | 32.0007 | 891.3714
5895.0062 | 27.8523 | 32.1076 | 894.2723
5910.0062 | 27.8532 | 31.9791 | 890.7191
5925.0061 | 27.8536 | 32.0806 | 893.5596
5940.0061 | 27.8527 | 32.0915 | 893.8344
5955.0062 | 27.854 | 32.0832 | 893.6453
5970.0061 | 27.8536 | 32.0672 | 893.186
5985.0062 | 27.8532 | 32.0829 | 893.6095
6000.0062 | 27.8548 | 32.1006 | 894.1548
6015.0062 | 27.8514 | 32.1223 | 894.6504
6030.0062 | 27.6794 | 29.4989 | 816.511
6045.0062 | 27.849 | 32.107 | 894.1475
6060.0062 | 27.8517 | 32.0429 | 892.4499
6075.0062 | 27.8545 | 32.0803 | 893.5796
6090.0062 | 27.8544 | 32.0453 | 892.6041
6105.0061 | 27.8544 | 32.1142 | 894.5199
6120.0061 | 27.8569 | 32.0335 | 892.3529
6135.0062 | 27.8573 | 32.0776 | 893.5951
6150.0061 | 27.8572 | 32.0074 | 891.6382
6165.0062 | 27.8575 | 32.052 | 892.8888
6180.0062 | 27.8577 | 32.0227 | 892.0781
6195.0061 | 27.8573 | 32.0617 | 893.1539
6210.0062 | 27.8576 | 32.0767 | 893.579
6225.0062 | 27.8581 | 32.1088 | 894.4908
6240.0061 | 27.8584 | 32.0484 | 892.8179
6255.0061 | 27.8593 | 32.0337 | 892.4346
6270.0061 | 27.8594 | 31.992 | 891.2788
6285.0061 | 27.8591 | 32.0322 | 892.3876
6300.0062 | 27.8609 | 32.0772 | 893.6996
6315.0062 | 27.8592 | 32.1169 | 894.752
6330.0062 | 27.8586 | 32.0341 | 892.426
6345.0061 | 27.8586 | 32.0056 | 891.6313
6360.0062 | 27.8606 | 32.0855 | 893.9235
6375.0061 | 27.8611 | 31.9817 | 891.0458
6390.0062 | 27.8616 | 32.0867 | 893.9862
6405.0061 | 27.8616 | 32.1076 | 894.5685
6420.0062 | 27.8613 | 32.0692 | 893.4917
6435.0062 | 27.8625 | 32.0274 | 892.3622
6450.0061 | 27.8616 | 32.0554 | 893.114
6465.0062 | 27.8606 | 32.1408 | 895.4633
6480.0062 | 27.8647 | 32.0845 | 894.0231
6495.0062 | 27.8632 | 32.0413 | 892.7729
6510.0062 | 27.8631 | 32.0927 | 894.2022
6525.0061 | 27.8623 | 32.1243 | 895.0562
6540.0061 | 27.8653 | 32.0389 | 892.776
6555.0061 | 27.8653 | 32.016 | 892.1354
6570.0061 | 27.865 | 32.1301 | 895.3039
6585.0062 | 27.8655 | 31.9879 | 891.3559
6600.0062 | 27.8643 | 32.0914 | 894.2041
6615.0061 | 27.8643 | 32.0042 | 891.7733
6630.0062 | 27.689 | 29.4237 | 814.7141
6645.0061 | 27.8578 | 32.0435 | 892.6617
6660.0062 | 27.8609 | 32.0261 | 892.2748
6675.0061 | 27.8603 | 32.1129 | 894.6721
6690.0062 | 27.8616 | 32.0172 | 892.0488
6705.0061 | 27.8641 | 32.0449 | 892.9028
6720.0062 | 27.8639 | 32.0894 | 894.1369
6735.0061 | 27.8637 | 32.0277 | 892.4106
6750.0061 | 27.866 | 32.039 | 892.8012
6765.0062 | 27.8659 | 32.1054 | 894.6466
6780.0062 | 27.8668 | 32.0336 | 892.6735
6795.0062 | 27.8673 | 32.1211 | 895.1278
6810.0061 | 27.8645 | 32.0671 | 893.5332
6825.0062 | 27.8665 | 32.0558 | 893.2845
6840.0062 | 27.8661 | 32.0062 | 891.8863
6855.0062 | 27.8687 | 32.0457 | 893.0707
6870.0062 | 27.867 | 32.0627 | 893.4896
6885.0062 | 27.8672 | 32.0335 | 892.6859
6900.0062 | 27.868 | 32.0488 | 893.135
6915.0061 | 27.8683 | 31.9666 | 890.8533
6930.0062 | 27.8674 | 32.0284 | 892.5494
6945.0062 | 27.8671 | 32.0468 | 893.0512
6960.0062 | 27.8669 | 32.031 | 892.6038
6975.0061 | 27.8673 | 32.0731 | 893.7904
6990.0062 | 27.8669 | 32.0617 | 893.4599
7005.0061 | 27.8686 | 32.1126 | 894.934
7020.0062 | 27.8665 | 32.0616 | 893.4424
7035.0062 | 27.8681 | 32.0603 | 893.4603
7050.0062 | 27.8708 | 32.0043 | 891.9852
7065.0062 | 27.8698 | 31.9994 | 891.8176
7080.0062 | 27.8698 | 31.981 | 891.3023
7095.0061 | 27.8676 | 32.0668 | 893.6253
7110.0062 | 27.8711 | 32.0701 | 893.8266
7125.0062 | 27.8689 | 32.0246 | 892.4891
7140.0062 | 27.8706 | 32.0051 | 892.0017
7155.0062 | 27.8699 | 31.9897 | 891.5509
7170.0061 | 27.8716 | 32.0074 | 892.0973
7185.0061 | 27.8707 | 32.0126 | 892.2136
7200.0062 | 27.8695 | 32.0079 | 892.0451
7215.0061 | 27.8737 | 32.094 | 894.5775
7230.0062 | 27.7123 | 28.7761 | 797.4516
7245.0062 | 27.8661 | 32.0353 | 892.699
7260.0061 | 27.8689 | 32.0891 | 894.2875
7275.0062 | 27.8704 | 32.0634 | 893.62
7290.0062 | 27.8717 | 32.0633 | 893.6559
7305.0062 | 27.8724 | 32.0221 | 892.5337
7320.0062 | 27.874 | 31.9446 | 890.4244
7335.0062 | 27.8721 | 32.0465 | 893.2028
7350.0062 | 27.8754 | 32.0296 | 892.8366
7365.0062 | 27.8754 | 32.025 | 892.7077
7380.0062 | 27.8758 | 31.9986 | 891.9838
7395.0062 | 27.8773 | 32.0035 | 892.1704
7410.0062 | 27.8763 | 31.9495 | 890.6335
7425.0062 | 27.8758 | 32.015 | 892.4436
7440.0062 | 27.877 | 32.0605 | 893.7501
7455.0061 | 27.8766 | 32.0056 | 892.2078
7470.0062 | 27.878 | 32.0004 | 892.1068
7485.0062 | 27.8766 | 32.0193 | 892.5902
7500.0062 | 27.876 | 32.0668 | 893.8938
7515.0062 | 27.876 | 31.9943 | 891.8748
7530.0062 | 27.8783 | 32.0358 | 893.1034
7545.0062 | 27.8779 | 32.0507 | 893.5077
7560.0062 | 27.8781 | 32.076 | 894.2168
7575.0062 | 27.8786 | 32.0125 | 892.4631
7590.0062 | 27.8782 | 32.0454 | 893.3689
7605.0061 | 27.8771 | 32.0142 | 892.4626
7620.0062 | 27.8802 | 31.9969 | 892.0801
7635.0062 | 27.8786 | 32.0621 | 893.8462
7650.0062 | 27.8802 | 32.0277 | 892.9385
7665.0062 | 27.8814 | 32.0211 | 892.7929
7680.0062 | 27.8804 | 31.9022 | 889.4457
7695.0061 | 27.8809 | 32.0704 | 894.1507
7710.0061 | 27.8817 | 31.9976 | 892.1458
7725.0062 | 27.8822 | 32.0612 | 893.9352
7740.0061 | 27.8846 | 32.06 | 893.982
7755.0062 | 27.8811 | 32.0575 | 893.7972
7770.0062 | 27.8836 | 32.0596 | 893.9383
7785.0061 | 27.8855 | 32.0743 | 894.4097
7800.0061 | 27.8845 | 32.05 | 893.6971
7815.0062 | 27.8832 | 32.03 | 893.0982
7830.0061 | 27.7601 | 32.0302 | 889.1608
7845.0062 | 27.8801 | 31.9733 | 891.4201
7860.0062 | 27.8842 | 32.0525 | 893.7595
7875.0062 | 27.8835 | 32.0239 | 892.9376
7890.0062 | 27.8831 | 32.0502 | 893.6588
7905.0062 | 27.8873 | 32.0386 | 893.4694
7920.0062 | 27.8859 | 32.0944 | 894.9807
7935.0062 | 27.8872 | 32.04 | 893.5038
7950.0061 | 27.8861 | 32.0141 | 892.7499
7965.0062 | 27.889 | 32.0141 | 892.8421
7980.0062 | 27.8873 | 31.9288 | 890.4105
7995.0062 | 27.8889 | 32.0453 | 893.7074
8010.0062 | 27.8878 | 32.0114 | 892.7247
8025.0062 | 27.8894 | 32.064 | 894.2452
8040.0062 | 27.888 | 31.9672 | 891.4999
8055.0062 | 27.8902 | 31.8802 | 889.1451
8070.0062 | 27.8902 | 31.991 | 892.235
8085.0062 | 27.8892 | 31.9616 | 891.3821
8100.0062 | 27.8896 | 31.9464 | 890.9714
8115.0062 | 27.8892 | 31.9917 | 892.2222
8130.0062 | 27.8898 | 32.0257 | 893.1904
8145.0062 | 27.8889 | 31.9438 | 890.8769
8160.0062 | 27.8899 | 32.0182 | 892.9849
8175.0062 | 27.8916 | 32.029 | 893.3392
8190.0061 | 27.8913 | 31.973 | 891.767
8205.0061 | 27.8913 | 32.0213 | 893.115
8220.0062 | 27.8939 | 32.0612 | 894.3121
8235.0062 | 27.8939 | 31.9675 | 891.6992
8250.0062 | 27.8942 | 32.0701 | 894.5718
8265.0061 | 27.8949 | 32.0107 | 892.9348
8280.0061 | 27.8958 | 32.0368 | 893.6929
8295.0062 | 27.8974 | 31.9723 | 891.9441
8310.0062 | 27.8951 | 32.022 | 893.2576
8325.0061 | 27.8969 | 31.9373 | 890.952
8340.0062 | 27.8987 | 31.9447 | 891.2149
8355.0062 | 27.8978 | 32.0239 | 893.3955
8370.0062 | 27.899 | 31.9433 | 891.1849
8385.0062 | 27.8972 | 31.9654 | 891.7425
8400.0062 | 27.8986 | 31.9545 | 891.4866
8415.0061 | 27.8977 | 32.0482 | 894.071
8430.0062 | 27.7509 | 27.7264 | 769.4308
8445.0061 | 27.8942 | 31.9389 | 890.9114
8460.0061 | 27.8939 | 32.0242 | 893.2797
8475.0061 | 27.8983 | 31.9486 | 891.3129
8490.0061 | 27.9003 | 31.9376 | 891.0704
8505.0062 | 27.9011 | 31.9479 | 891.3829
8520.0062 | 27.9018 | 31.9669 | 891.9348
8535.0062 | 27.9038 | 32.0302 | 893.7632
8550.0062 | 27.9022 | 32.0165 | 893.3315
8565.0061 | 27.9041 | 31.9336 | 891.0805
8580.0062 | 27.9043 | 31.9921 | 892.7161
8595.0062 | 27.9042 | 31.9774 | 892.3031
8610.0061 | 27.9054 | 31.9826 | 892.4882
8625.0062 | 27.9067 | 31.9643 | 892.0162
8640.0061 | 27.9062 | 32.0304 | 893.8486
8655.0062 | 27.9066 | 31.9699 | 892.1717
8670.0062 | 27.9107 | 32.0037 | 893.244
8685.0062 | 27.9102 | 31.9536 | 891.8318
8700.0061 | 27.9106 | 31.9924 | 892.9256
8715.0062 | 27.9117 | 31.996 | 893.0633
8730.0062 | 27.9117 | 32.0162 | 893.6283
8745.0061 | 27.9132 | 32.0662 | 895.0688
8760.0061 | 27.9127 | 31.9708 | 892.3921
8775.0062 | 27.9123 | 31.953 | 891.8827
8790.0061 | 27.9134 | 31.9965 | 893.1295
8805.0062 | 27.9135 | 32.0071 | 893.4289
8820.0061 | 27.9152 | 31.9265 | 891.2356
8835.0062 | 27.9159 | 32.0422 | 894.4865
8850.0062 | 27.9166 | 31.9551 | 892.0767
8865.0062 | 27.9145 | 32.0437 | 894.4839
8880.0062 | 27.916 | 32.0233 | 893.9628
8895.0062 | 27.9175 | 32.0248 | 894.0534
8910.0062 | 27.9188 | 31.9653 | 892.434
8925.0062 | 27.9188 | 32.0165 | 893.8622
8940.0062 | 27.9168 | 32.0544 | 894.8567
8955.0062 | 27.9185 | 32.0216 | 893.9944
8970.0062 | 27.9204 | 32.0024 | 893.5196
8985.0061 | 27.9217 | 32.0083 | 893.7241
9000.0062 | 27.9214 | 32.0464 | 894.7813
9015.0062 | 27.9212 | 32.0433 | 894.6862
9030.0062 | 27.7774 | 27.1806 | 755.0069
9045.0062 | 27.9146 | 31.9915 | 893.0319
9060.0062 | 27.9165 | 31.9369 | 891.5648
9075.0062 | 27.9211 | 32.0285 | 894.2697
9090.0062 | 27.9229 | 31.9748 | 892.8275
9105.0061 | 27.9231 | 32.0096 | 893.8084
9120.0061 | 27.9246 | 32.0177 | 894.0822
9135.0062 | 27.9257 | 31.8905 | 890.5639
9150.0062 | 27.9289 | 31.9765 | 893.0685
9165.0062 | 27.9301 | 31.9619 | 892.6988
9180.0062 | 27.9282 | 31.9587 | 892.5484
9195.0062 | 27.9301 | 31.9307 | 891.8283
9210.0062 | 27.9325 | 31.9601 | 892.7271
9225.0062 | 27.9336 | 31.9088 | 891.3298
9240.0062 | 27.9338 | 32.0042 | 893.9999
9255.0062 | 27.9343 | 31.9176 | 891.5952
9270.0061 | 27.9336 | 31.9623 | 892.8234
9285.0062 | 27.9357 | 31.932 | 892.0453
9300.0061 | 27.9375 | 32.0328 | 894.9151
9315.0062 | 27.9378 | 31.9876 | 893.6652
9330.0062 | 27.9397 | 32.0161 | 894.5205
9345.0062 | 27.9389 | 31.9905 | 893.7808
9360.0062 | 27.94 | 32.0341 | 895.0336
9375.0062 | 27.9398 | 31.8786 | 890.682
9390.0062 | 27.942 | 31.9164 | 891.809
9405.0062 | 27.9418 | 31.9131 | 891.7078
9420.0062 | 27.9437 | 31.941 | 892.5482
9435.0062 | 27.9412 | 31.9179 | 891.8251
9450.0062 | 27.9446 | 31.9751 | 893.5317
9465.0062 | 27.9454 | 31.9021 | 891.517
9480.0062 | 27.9478 | 31.9998 | 894.3236
9495.0062 | 27.9487 | 31.9892 | 894.0565
9510.0062 | 27.9485 | 31.8666 | 890.6237
9525.0062 | 27.9486 | 31.9533 | 893.0482
9540.0062 | 27.9489 | 31.9133 | 891.9406
9555.0062 | 27.9523 | 31.9574 | 893.2816
9570.0062 | 27.9526 | 31.8121 | 889.2315
9585.0062 | 27.9516 | 31.9338 | 892.6004
9600.0061 | 27.9536 | 31.9618 | 893.4468
9615.0062 | 27.9538 | 31.9835 | 894.061
9630.0062 | 27.8031 | 27.0938 | 753.2938
9645.0062 | 27.947 | 31.934 | 892.4613
9660.0062 | 27.9507 | 31.9494 | 893.0086
9675.0062 | 27.9533 | 31.9255 | 892.4218
9690.0062 | 27.9575 | 31.9104 | 892.1363
9705.0062 | 27.9599 | 31.9524 | 893.3864
9720.0061 | 27.9593 | 31.8981 | 891.8479
9735.0062 | 27.9624 | 31.935 | 892.9803
9750.0062 | 27.9625 | 31.8603 | 890.8918
9765.0062 | 27.9625 | 31.8802 | 891.4489
9780.0062 | 27.9665 | 31.9669 | 894.0031
9795.0062 | 27.9675 | 31.8986 | 892.1251
9810.0062 | 27.968 | 31.904 | 892.2921
9825.0062 | 27.9695 | 31.8839 | 891.7757
9840.0061 | 27.9719 | 31.9313 | 893.1803
9855.0062 | 27.9721 | 31.9261 | 893.0399
9870.0062 | 27.9727 | 31.9454 | 893.6002
9885.0061 | 27.9751 | 31.9764 | 894.5416
9900.0062 | 27.9755 | 31.8468 | 890.9294
9915.0062 | 27.978 | 31.861 | 891.4066
9930.0062 | 27.9793 | 31.8817 | 892.0269
9945.0062 | 27.9812 | 31.9212 | 893.1944
9960.0062 | 27.9831 | 31.9596 | 894.3283
9975.0062 | 27.9836 | 31.9145 | 893.0817
9990.0061 | 27.9851 | 31.9015 | 892.7658
10005.0062 | 27.9861 | 31.9558 | 894.3186
10020.0062 | 27.9876 | 31.8582 | 891.6357
10035.0062 | 27.9895 | 31.9423 | 894.0499
10050.0062 | 27.9913 | 31.9017 | 892.9699
10065.0062 | 27.994 | 31.9002 | 893.012
10080.0062 | 27.9924 | 31.9151 | 893.3784
10095.0062 | 27.9966 | 31.8965 | 892.9923
10110.0062 | 27.9975 | 31.9206 | 893.6985
10125.0062 | 27.9982 | 31.9539 | 894.6509
10140.0062 | 28.0016 | 31.8772 | 892.6125
10155.0062 | 27.999 | 31.8742 | 892.445
10170.0062 | 28.0033 | 31.8725 | 892.5338
10185.0062 | 28.007 | 31.8997 | 893.4156
10200.0061 | 28.0058 | 31.7983 | 890.5377
10215.0062 | 28.0085 | 31.8368 | 891.7036
10230.0062 | 27.9307 | 27.4899 | 767.8117
10245.0061 | 28.0013 | 31.8593 | 892.1009
10260.0062 | 28.0051 | 31.9037 | 893.4641
10275.0061 | 28.0109 | 31.8193 | 891.2848
10290.0062 | 28.014 | 31.8766 | 892.9924
10305.0062 | 28.0178 | 31.9008 | 893.7887
10320.0062 | 28.0185 | 31.7284 | 888.9809
10335.0062 | 28.0217 | 31.9146 | 894.3032
10350.0062 | 28.0266 | 31.8973 | 893.9718
10365.0062 | 28.0276 | 31.8504 | 892.6891
10380.0062 | 28.0302 | 31.8503 | 892.769
10395.0062 | 28.0327 | 31.8954 | 894.1153
10410.0062 | 28.0339 | 31.8773 | 893.6452
10425.0062 | 28.0363 | 31.9312 | 895.2343
10440.0061 | 28.0415 | 31.8627 | 893.4785
10455.0062 | 28.0434 | 31.8927 | 894.3802
10470.0062 | 28.045 | 31.924 | 895.307
10485.0062 | 28.0465 | 31.8667 | 893.7493
10500.0061 | 28.0512 | 31.8894 | 894.5352
10515.0061 | 28.0552 | 31.8437 | 893.379
10530.0062 | 28.0559 | 31.9176 | 895.4785
10545.0061 | 28.0567 | 31.8595 | 893.8738
10560.0062 | 28.0598 | 31.7819 | 891.7939
10575.0062 | 28.0639 | 31.8005 | 892.4463
10590.0062 | 28.067 | 31.8152 | 892.9564
10605.0061 | 28.0681 | 31.8673 | 894.453
10620.0062 | 28.0738 | 31.8676 | 894.6449
10635.0061 | 28.0767 | 31.845 | 894.1033
10650.0062 | 28.0799 | 31.8012 | 892.9739
10665.0062 | 28.0808 | 31.8318 | 893.862
10680.0062 | 28.0856 | 31.8025 | 893.1949
10695.0062 | 28.0885 | 31.8272 | 893.98
10710.0062 | 28.0939 | 31.7606 | 892.2768
10725.0062 | 28.0967 | 31.8174 | 893.9629
10740.0062 | 28.1002 | 31.8135 | 893.9654
10755.0061 | 28.1042 | 31.761 | 892.6181
10770.0062 | 28.1085 | 31.7629 | 892.8061
10785.0062 | 28.1132 | 31.7839 | 893.5481
10800.0061 | 28.1177 | 31.6896 | 891.0363
10815.0061 | 28.1228 | 30.2779 | 851.4993
10830.0062 | 28.0786 | 31.7607 | 891.7971
10845.0061 | 28.1262 | 31.7368 | 892.6357
10860.0062 | 28.1303 | 31.6824 | 891.2342
10875.0062 | 28.1379 | 31.7296 | 892.805
10890.0062 | 28.1437 | 31.7971 | 894.8896
10905.0061 | 28.1499 | 31.6826 | 891.8593
10920.0062 | 28.1564 | 31.7299 | 893.3992
10935.0062 | 28.163 | 31.7201 | 893.3354
10950.0062 | 28.1683 | 31.7237 | 893.6032
10965.0062 | 28.1748 | 31.686 | 892.7455
10980.0062 | 28.1835 | 31.7025 | 893.4875
10995.0062 | 28.1892 | 31.6718 | 892.8034
11010.0062 | 28.1981 | 31.6843 | 893.4356
11025.0062 | 28.204 | 31.6527 | 892.7338
11040.0062 | 28.2129 | 31.6516 | 892.981
11055.0062 | 28.2196 | 31.607 | 891.9345
11070.0062 | 28.2292 | 31.6165 | 892.5099
11085.0062 | 28.2395 | 31.6142 | 892.7706
11100.0062 | 28.2474 | 31.6569 | 894.2251
11115.0062 | 28.2581 | 31.6214 | 893.5627
11130.0062 | 28.2666 | 31.5424 | 891.5961
11145.0062 | 28.28 | 31.5077 | 891.0395
11160.0062 | 28.2893 | 31.5439 | 892.3545
11175.0061 | 28.3047 | 31.5667 | 893.4868
11190.0062 | 28.3148 | 31.5754 | 894.0535
11205.0062 | 28.3294 | 31.61 | 895.4899
11220.0062 | 28.3432 | 31.5052 | 892.9573
11235.0062 | 28.36 | 31.4865 | 892.9574
11250.0062 | 28.3763 | 31.4987 | 893.8169
11265.0062 | 28.3945 | 31.5176 | 894.9252
11280.0062 | 28.4131 | 31.4408 | 893.3302
11295.0062 | 28.433 | 31.487 | 895.2698
11310.0062 | 28.4554 | 31.3712 | 892.6814
11325.0062 | 28.4706 | 31.1336 | 886.3928
11340.0062 | 28.494 | 31.0822 | 885.6573
11355.0062 | 28.4861 | 29.8187 | 849.417
11370.0062 | 28.4937 | 29.377 | 837.0588
11385.0062 | 28.5024 | 28.8759 | 823.0345
11400.0062 | 28.5044 | 28.1739 | 803.0791
11415.0062 | 28.5128 | 27.663 | 788.7492
11430.0062 | 28.5158 | 26.9416 | 768.2622
11445.0062 | 28.5246 | 26.4407 | 754.2121
11460.0061 | 28.534 | 25.6641 | 732.2985
11475.0062 | 28.5364 | 25.1722 | 718.3226
11490.0062 | 28.5457 | 24.6434 | 703.4636
11505.0062 | 28.5473 | 23.8701 | 681.4246
11520.0062 | 28.5568 | 23.4012 | 668.2649
11535.0062 | 28.5621 | 22.6221 | 646.1362
11550.0062 | 28.5677 | 22.1212 | 631.9525
11565.0062 | 28.5768 | 21.6197 | 617.8217
11580.0061 | 28.5789 | 20.9001 | 597.3003
11595.0062 | 28.5884 | 20.397 | 583.1184
11610.0061 | 28.5904 | 19.6768 | 562.5677
11625.0062 | 28.5983 | 19.1848 | 548.6541
11640.0062 | 28.6071 | 18.6111 | 532.4101
11655.0062 | 28.6082 | 18.0365 | 515.9939
11670.0062 | 28.6168 | 17.5617 | 502.5602
11685.0062 | 28.6182 | 16.9061 | 483.8205
11700.0062 | 28.6255 | 16.474 | 471.5749
11715.0062 | 28.6337 | 15.9177 | 455.7827
11730.0062 | 28.2693 | -0.0030654 | -0.086656
11745.0062 | 28.0567 | -0.0030628 | -0.085932
11760.0062 | 27.9619 | -0.0031173 | -0.087166
11775.0061 | 27.891 | -0.0030227 | -0.084305
11790.0062 | 27.8344 | -0.0031683 | -0.088188
11805.0062 | 27.7871 | -0.0031591 | -0.087783
11820.0062 | 27.7465 | -0.003096 | -0.085903
11835.0062 | 27.7108 | -0.0030931 | -0.085712
11850.0062 | 27.6788 | -0.0031949 | -0.088431
11865.0062 | 27.6499 | -0.0031369 | -0.086735
11880.0062 | 27.6235 | -0.0030644 | -0.08465
11895.0062 | 27.5992 | -0.0031652 | -0.087358
11910.0062 | 27.5769 | -0.0030334 | -0.083651
11925.0062 | 27.556 | -0.0030473 | -0.083972
11940.0062 | 27.5366 | -0.0030311 | -0.083467
11955.0062 | 27.5183 | -0.0031016 | -0.08535
11970.0062 | 27.5013 | -0.0029637 | -0.081506
11985.0062 | 27.4851 | -0.0029173 | -0.080182
12000.0062 | 27.4699 | -0.0028956 | -0.079542
12015.0062 | 27.4555 | -0.0028026 | -0.076946
12030.0062 | 27.4419 | -0.0028434 | -0.078029
12045.0062 | 27.429 | -0.0029042 | -0.079659
12060.0062 | 27.4166 | -0.0028073 | -0.076966
12075.0062 | 27.4048 | -0.0029756 | -0.081546
12090.0062 | 27.3936 | -0.0029294 | -0.080247
12105.0062 | 27.3828 | -0.0029204 | -0.07997
12120.0062 | 27.3726 | -0.0028485 | -0.077971
12135.0062 | 27.3627 | -0.0028102 | -0.076896
12150.0062 | 27.3533 | -0.0028469 | -0.077873
12165.0062 | 27.3442 | -0.0027733 | -0.075834
12180.0062 | 27.3354 | -0.0027579 | -0.075389
12195.0062 | 27.327 | -0.0029295 | -0.080055
12210.0062 | 27.3189 | -0.0027567 | -0.075311
12225.0062 | 27.3111 | -0.0027673 | -0.075579
12240.0062 | 27.3036 | -0.0027184 | -0.074223
12255.0062 | 27.2963 | -0.0027687 | -0.075576
12270.0062 | 27.2892 | -0.002826 | -0.077119
12285.0062 | 27.2824 | -0.0028297 | -0.0772
12300.0062 | 27.2758 | -0.0028516 | -0.077779
12315.0062 | 27.2694 | -0.0028544 | -0.077839
12330.0062 | 27.2632 | -0.0027494 | -0.074958
12345.0061 | 27.2572 | -0.0027369 | -0.074601
12360.0062 | 27.2514 | -0.0027531 | -0.075025
12375.0062 | 27.2457 | -0.0028177 | -0.07677
12390.0062 | 27.2402 | -0.0026223 | -0.071431
12405.0062 | 27.2348 | -0.0026488 | -0.07214
12420.0062 | 27.2296 | -0.0025738 | -0.070084
12435.0062 | 27.2246 | -0.0027163 | -0.073949
12450.0062 | 27.2196 | -0.0026673 | -0.072603
12465.0062 | 27.2148 | -0.0025661 | -0.069835
12480.0062 | 27.2102 | -0.002715 | -0.073877
12495.0061 | 27.2056 | -0.0026901 | -0.073186
12510.0062 | 27.2012 | -0.0026645 | -0.072477
12525.0062 | 27.1968 | -0.0027219 | -0.074026
12540.0062 | 27.1926 | -0.0027764 | -0.075498
12555.0062 | 27.1885 | -0.0027946 | -0.07598
12570.0062 | 27.1845 | -0.002813 | -0.07647
12585.0062 | 27.1805 | -0.0026526 | -0.072099
12600.0062 | 27.1767 | -0.002707 | -0.073568
12615.0062 | 27.1729 | -0.0027677 | -0.075207
12630.0062 | 27.1693 | -0.0027631 | -0.075072
12645.0062 | 27.1657 | -0.0026639 | -0.072366
12660.0062 | 27.1621 | -0.002687 | -0.072985
12675.0062 | 27.1587 | -0.0025776 | -0.070005
12690.0062 | 27.1553 | -0.0025481 | -0.069193
12705.0062 | 27.152 | -0.0025372 | -0.06889
12720.0062 | 27.1488 | -0.0026411 | -0.071702
12735.0062 | 27.1457 | -0.0026013 | -0.070614
12750.0062 | 27.1426 | -0.0025754 | -0.069904
12765.0062 | 27.1395 | -0.00256 | -0.069478
12780.0062 | 27.1366 | -0.002624 | -0.071206
12795.0062 | 27.1337 | -0.0025998 | -0.070543
12810.0062 | 27.1308 | -0.0025726 | -0.069796
12825.0062 | 27.128 | -0.0025945 | -0.070383
12840.0062 | 27.1252 | -0.0025712 | -0.069745
12855.0062 | 27.1225 | -0.0025235 | -0.068444
12870.0062 | 27.1199 | -0.0024765 | -0.067163
12885.0062 | 27.1173 | -0.0025894 | -0.070218
12900.0062 | 27.1148 | -0.0026529 | -0.071934
12915.0062 | 27.1123 | -0.0026503 | -0.071854
12930.0062 | 27.1099 | -0.0026156 | -0.070908
12945.0062 | 27.1074 | -0.0024863 | -0.067399
12960.0062 | 27.1051 | -0.00256 | -0.069388
12975.0062 | 27.1027 | -0.0025539 | -0.069218
12990.0061 | 27.1004 | -0.0025061 | -0.067916
13005.0062 | 27.0982 | -0.002564 | -0.06948
13020.0062 | 27.0959 | -0.0026331 | -0.071347
13035.0062 | 27.0938 | -0.0025876 | -0.070107
13050.0062 | 27.0916 | -0.0025561 | -0.069248
13065.0062 | 27.0895 | -0.002579 | -0.069863
13080.0062 | 27.0875 | -0.0025883 | -0.07011
13095.0062 | 27.0854 | -0.0025778 | -0.069821
13110.0062 | 27.0834 | -0.0025324 | -0.068585
13125.0062 | 27.0814 | -0.002475 | -0.067026
13140.0062 | 27.0794 | -0.0024784 | -0.067114
13155.0062 | 27.0776 | -0.0025815 | -0.0699
13170.0061 | 27.0756 | -0.0026458 | -0.071637
13185.0062 | 27.0738 | -0.0024718 | -0.066922
13200.0062 | 27.072 | -0.0025355 | -0.068642
13215.0062 | 27.0701 | -0.0025297 | -0.068478
13230.0062 | 27.0683 | -0.0025505 | -0.069039
13245.0062 | 27.0666 | -0.0025223 | -0.068271
13260.0062 | 27.0649 | -0.0025601 | -0.069289
13275.0062 | 27.0632 | -0.0025718 | -0.0696
13290.0062 | 27.0614 | -0.002629 | -0.071145
13305.0062 | 27.0598 | -0.0026305 | -0.071182
13320.0062 | 27.0582 | -0.0025257 | -0.068341
13335.0062 | 27.0566 | -0.002462 | -0.066614
13350.0062 | 27.055 | -0.002552 | -0.069043
13365.0062 | 27.0535 | -0.002562 | -0.069311
13380.0062 | 27.0519 | -0.0025308 | -0.068463
13395.0062 | 27.0503 | -0.0025607 | -0.069267
13410.0062 | 27.0488 | -0.0025326 | -0.068503
13425.0062 | 27.0474 | -0.0025576 | -0.069178
13440.0062 | 27.0459 | -0.0025947 | -0.070175
13455.0062 | 27.0445 | -0.0025762 | -0.069672
13470.0062 | 27.043 | -0.0026211 | -0.070884

## batt_info
CALB L-Series L173F230
Nominal Capacity | 230 | Ah
Measured Capacity | 250.3906 | Ah
Nominal Voltage | 3.2 | V
Internal Resistance @ 1kHz AC | 0.2-0.5 | mOhm
Charging Allowable Maximum Current | Based on SOC & temperature
Charging Voltage Limit | 3.65 | V
Charging Temperature Limits (C) | -5 to 60 | °C
Charging Temperature Limits (F) | 23 to 140 | °F
Discharging Maximum Continuous Current | 230 | A
Discharging Pulse Current; Up to 3 minutes | 460 | A
Discharging Pulse Current; Up to 30 seconds | 690 | A
Discharging Voltage Limit | 2.5 | V
Discharging Temperature Limits (C) | -20 to 55 | °C
Discharging Temperature Limits (F) | -4 to 131 | °F
Storage State of Charge (SoC) | 30 | %
Storage OCV correlating to 30% SoC | 3.275 to 3.305 | V
Storage Short Term Ambient Temp (C) | -20 to 45 | °C
Storage Short Term Ambient Temp (F) | -4 to 113 | °F
Storage Long Term Ambient Temp (C) | -5 to 25 | °C
Storage Long Term Ambient Temp (F) | -4 to 77 | °F
Storage Humidity | ≤70 | %
Weight | 9.26 | lbs | 148.16 | lbs for 16 cells
Length | 173.9 | mm
Width | 53.7 | mm
Height (excludes terminals and bussing) | 217.9 | mm